## Sheet1
Table 1 OutBack Block
Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | OutBack_DID | uint16 | N/A | N/A | 64110 | Uniquely identifies this as a SunSpec Outback Interface
2 | 2 | 1 | R | OutBack_Length | uint16 | Registers | N/A | 405 | Length of block in 16-bit registers
3 | 3 | 1 | R | OutBack_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | OutBack Major firmware revision
4 | 4 | 1 | R | OutBack_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | OutBack Mid firmware revision
5 | 6 | 1 | R | OutBack_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | OutBack Minor firmware revision
6 | 6 | 1 | R | OutBack_Encryption_Key | uint16 | N/A | N/A | Read Only | Encryption key for current session (0 = Encryption not enabled)
7 | 13 | 7 | R | OutBack_MAC_Address | string (14) | N/A | N/A | Read Only | Ethernet MAC address
14 | 21 | 8 | W | OutBack_Write_Password | string (16) | N/A | N/A | Write Only | Password required to write to any register
22 | 22 | 1 | R/W | OutBack_Enable_DHCP | uint16 | Enumerated | N/A | Programmable | 0 = DHCP Disabled, use configured network parameter; 1 = DHCP Enabled
23 | 24 | 2 | R/W | OutBack_TCP/IP_Address | uint32 | Address | N/A | Programmable | TCP/IP Address xxx.xxx.xxx.xxx
25 | 26 | 2 | R/W | OutBack_TCP/IP_Gateway_MSW | uint32 | Address | N/A | Programmable | TCP/IP Gateway xxx.xxx.xxx.xxx
27 | 28 | 2 | R/W | OutBack_TCP/IP_Netmask_MSW | uint32 | Address | N/A | Programmable | TCP/IP Netmask xxx.xxx.xxx.xxx
29 | 30 | 2 | R/W | OutBack_TCP/IP_DNS_1_MSW | uint32 | Address | N/A | Programmable | TCP/IP DNS 1 xxx.xxx.xxx.xxx
31 | 32 | 2 | R/W | OutBack_TCP/IP_DNS_2_MSW | uint32 | Address | N/A | Programmable | TCP/IP DNS 2 xxx.xxx.xxx.xxx
33 | 33 | 1 | R/W | OutBack_Modbus_Port | uint16 | N/A | N/A | Programmable | Outback MODBUS IP port, default 502
34 | 53 | 20 | R/W | OutBack_SMTP_Server_Name | string (40) | N/A | N/A | Programmable | Email server name
54 | 69 | 16 | R/W | OutBack_SMTP_Account_Name | string (32) | N/A | N/A | Programmable | Email account name
70 | 70 | 1 | R/W | OutBack_SMTP_SSL_Enable | uint16 | Enumerated | N/A | Programmable | 0 = SSL Disabled; 1 = SSL Enabled (not implemented)
71 | 78 | 8 | W | OutBack_SMTP_Email_Password | string 16) | N/A | N/A | Write Only | Email account password
79 | 98 | 20 | R/W | OutBack_SMTP_Email_User_Name | string (40) | N/A | N/A | Programmable | Email account User Name
99 | 99 | 1 | R/W | OutBack_Status_Email_Interval | uint16 | N/A | N/A | Programmable | 0 = Status Email Disabled, 1-23 Status Email every n hours
100 | 100 | 1 | R/W | OutBack_Status_Email_Status_Time | uint16 | N/A | N/A | Programmable | Hour of first status email of the day
101 | 125 | 25 | R/W | OutBack_Status_Email_Subject_Line | string (50) | N/A | N/A | Programmable | Status Email Subject Line
126 | 145 | 20 | R/W | OutBack_Status_Email_To_Address_1 | string (40) | N/A | N/A | Programmable | Status Email to Address 1
146 | 165 | 20 | R/W | OutBack_Status_Email_To_Address_2 | string (40) | N/A | N/A | Programmable | Status Email to Address 2
166 | 166 | 1 | R/W | OutBack_Alarm_Email_Enable | uint16 | Enumerated | N/A | Programmable | 0 = Disabled; 1 = Enabled
167 | 191 | 25 | R/W | OutBack_Alarm_Email_Subject_Line | string (50) | N/A | N/A | Programmable | Status Alarm_Subject Line
192 | 211 | 20 | R/W | OutBack_Alarm_Email_To_Address_1 | string (40) | N/A | N/A | Programmable | Status Alarm to Address 1
212 | 231 | 20 | R/W | OutBack_Alarm_Email_To_Address_2 | string (40) | N/A | N/A | Programmable | Status Alarm to Address 2
232 | 239 | 8 | W | OutBack_FTP_Password | string (16) | N/A | N/A | Write Only | FTP password
240 | 247 | 8 | W | OutBack_Telnet_Password | string (16) | N/A | N/A | Write Only | Telnet password (not implemented)
248 | 248 | 1 | R/W | OutBack_SD_Card_Data_Log_Write_Interval | uint16 | N/A | N/A | Programmable | 0 = SD-Card Data Logging disabled, 1-60 seconds
249 | 249 | 1 | R/W | OutBack_SD_Card_Data_Log_Retain_Days | uint16 | N/A | N/A | Programmable | 0 = Log until SD-Card is full then erase oldest, 1-731 Number of days to retain data logs
250 | 250 | 1 | R/W | OutBack_SD_Card_Data_Logging_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Disabled; 1 = Excel Format; 2 = Compact Format
251 | 270 | 20 | R/W | OutBack_Time_Server_Name | string (40) | N/A | N/A | Programmable | Timeserver domain name
271 | 271 | 1 | R/W | OutBack_Enable_Time_Server | uint16 | Enumerated | N/A | Programmable | 0 = Time Server Disabled, use configured time parameters; 1 = Time Server Enabled
272 | 272 | 1 | R/W | OutBack_Set_Time_Zone | int16 | Hours | N/A | Programmable | Time Zone -12-11
273 | 273 | 1 | R/W | OutBack_Enable_Float_Coordination | uint16 | N/A | N/A | Programmable | 0=Disabled, 1=Enabled
274 | 274 | 1 | R/W | OutBack_Enable_FNDC_Charge_Termination | uint16 | N/A | N/A | Programmable | 0=Disabled, 1=Enabled
275 | 275 | 1 | R/W | OutBack_Enable_FNDC_Grid_Tie_Control | uint16 | N/A | N/A | Programmable | 0=Disabled, 1=Enabled
276 | 276 | 1 | R | OutBack_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
277 | 277 | 1 | R | OutBack_Hour_SF | int16 | N/A | N/A | -1 | Hours Scale Factor
278 | 278 | 1 | R/W | OutBack_AGS_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
279 | 279 | 1 | R/W | OutBack_AGS_Port | uint16 | N/A | N/A | Programmable | AGS device port number 0-10
280 | 280 | 1 | R/W | OutBack_AGS_Port_Type | uint16 | Enumerated | N/A | Programmable | 0=Radian AUX Relay, 1=Radian AUX Output
281 | 281 | 1 | R/W | OutBack_AGS_Generator_Type | uint16 | Enumerated | N/A | Programmable | 0=AC Gen, 1=DC Gen, 2=No Gen
282 | 282 | 1 | R/W | OutBack_AGS_DC_Gen_Absorb_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | DC Generator Absorb Voltage
283 | 283 | 1 | R/W | OutBack_AGS_DC_Gen_Absorb_Time | uint16 | Hour | OutBack_Hour_SF | Programmable | DC Generator Absorb Time
284 | 284 | 1 | R/W | OutBack_AGS_Fault_Time | uint16 | Minutes | N/A | Programmable | AGS Generator fault time delay
285 | 285 | 1 | R/W | OutBack_AGS_Gen_Cool_Down_Time | uint16 | Minutes | N/A | Programmable | AGS Generator Cool Down Time
286 | 286 | 1 | R/W | OutBack_AGS_Gen_Warm_Up_Time | uint16 | Minutes | N/A | Programmable | AGS Generator Warm Up Time
287 | 287 | 1 | R/W | OutBack_AGS_Generator_Exercise_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
288 | 288 | 1 | R/W | OutBack_AGS_Exercise_Start_Hour | uint16 | Hour | N/A | Programmable | Exercise Start Hour 0-23
289 | 289 | 1 | R/W | OutBack_AGS_Exercise_Start_Minute | uint16 | Minutes | N/A | Programmable | Exercise Start Minute 0-59
290 | 290 | 1 | R/W | OutBack_AGS_Exercise_Day | uint16 | Enumerated | N/A | Programmable | 0=Sun, 1=Mon, 2=Tue, 3=Wed, 4=Thr, 5=Fri, 6=Sat
291 | 291 | 1 | R/W | OutBack_AGS_Exercise_Period | uint16 | Minutes | N/A | Programmable | Exercise Period 1-240 minutes
292 | 292 | 1 | R/W | OutBack_AGS_Exercise_Interval | uint16 | Weeks | N/A | Programmable | Exercise interval 1-8 Weeks
293 | 293 | 1 | R/W | OutBack_AGS_Sell_Mode | uint16 | Enumerated | N/A | Programmable | Sell During Generator Exercise Period, 0=Selling Enabled, 1=Selling Disabled
294 | 294 | 1 | R/W | OutBack_AGS_2_Min_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
295 | 295 | 1 | R/W | OutBack_AGS_2_Min_Start_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Two Minute AGS Start Voltage
296 | 296 | 1 | R/W | OutBack_AGS_2_Hour_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
297 | 297 | 1 | R/W | OutBack_AGS_2_Hour_Start_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Two Hour AGS Start Voltage
298 | 298 | 1 | R/W | OutBack_AGS_24_Hour_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
299 | 299 | 1 | R/W | OutBack_AGS_24_Hour_Start_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Twenty Four Hour AGS Start Voltage
300 | 300 | 1 | R/W | OutBack_AGS_Load_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
301 | 301 | 1 | R/W | OutBack_AGS_Load_Start_kW | uint16 | kWatts | N/A | Programmable | Load Start kWatts
302 | 302 | 1 | R/W | OutBack_AGS_Load_Start_Delay | uint16 | Minutes | N/A | Programmable | Load Start Delay
303 | 303 | 1 | R/W | OutBack_AGS_Load_Stop_kW | uint16 | kWatts | N/A | Programmable | Load Stop kWatts
304 | 304 | 1 | R/W | OutBack_AGS_Load_Stop_Delay | uint16 | Minutes | N/A | Programmable | Load Stop Delay
305 | 305 | 1 | R/W | OutBack_AGS_SOC_Start_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
306 | 306 | 1 | R/W | OutBack_AGS_SOC_Start_Percentage | uint16 | Percent | N/A | Programmable | AGS SOC Start Percentage
307 | 307 | 1 | R/W | OutBack_AGS_SOC_Stop_Percentage | uint16 | Percent | N/A | Programmable | AGS SOC Stop Percentage
308 | 308 | 1 | R/W | OutBack_AGS_Enable_Full_Charge_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
309 | 309 | 1 | R/W | OutBack_AGS_Full_Charge_Interval | uint16 | Days | N/A | Programmable | AGS SOC Full Charge Interval
310 | 310 | 1 | R/W | OutBack_AGS_Must_Run_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
311 | 311 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekday Start Hour 0-23
312 | 312 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekday Start Minute 0-59
313 | 313 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekday Stop Hour 0-23
314 | 314 | 1 | R/W | OutBack_AGS_Must_Run_Weekday_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekday Stop Minute 0-59
315 | 315 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekend Start Hour 0-23
316 | 316 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekend Start Minute 0-59
317 | 317 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Must Run Weekend Stop Hour 0-23
318 | 318 | 1 | R/W | OutBack_AGS_Must_Run_Weekend_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Must Run Weekend Stop Minute 0-59
319 | 319 | 1 | R/W | OutBack_AGS_Quiet_Time_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
320 | 320 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekday Start Hour 0-23
321 | 321 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekday Start Minute 0-59
322 | 322 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekday Stop Hour 0-23
323 | 323 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekday_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekday Stop Minute 0-59
324 | 324 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Start_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekend Start Hour 0-23
325 | 325 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Start_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekend Start Minute 0-59
326 | 326 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Stop_Hour | uint16 | Hour | N/A | Programmable | AGS Quiet Time Weekend Stop Hour 0-23
327 | 327 | 1 | R/W | OutBack_AGS_Quiet_Time_Weekend_Stop_Minute | uint16 | Minute | N/A | Programmable | AGS Quiet Time Weekend Stop Minute 0-59
328 | 329 | 2 | R/W | OutBack_AGS_Total_Generator_Run_Time | uint32 | Seconds | N/A | Programmable | AGS Generator Total Run Time in Seconds
330 | 330 | 1 | R/W | OutBack_HBX_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Voltage Only, 2=SOC Only, 3=Both
331 | 331 | 1 | R/W | OutBack_HBX_Grid_Connect_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | HBX Grid Connect Voltage
332 | 332 | 1 | R/W | OutBack_HBX_Grid_Connect_Delay | uint16 | Hours | OutBack_Hour_SF | Programmable | HBX Grid Connect Delay
333 | 333 | 1 | R/W | OutBack_HBX_Grid_Disconnect_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | HBX Grid Disconnect Voltage
334 | 334 | 1 | R/W | OutBack_HBX_Grid_Disconnect_Delay | uint16 | Hours | OutBack_Hour_SF | Programmable | HBX Grid Disconnect Delay
335 | 335 | 1 | R/W | OutBack_HBX_Grid_Connect_SOC | uint16 | Percent | N/A | Programmable | HBX Grid Connect SOC Percentage
336 | 336 | 1 | R/W | OutBack_HBX_Grid_Disconnect_SOC | uint16 | Percent | N/A | Programmable | HBX Grid Disconnect SOC Percentage
337 | 337 | 1 | R/W | OutBack_Grid_Use_Interval_1_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
338 | 338 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Start Hour 0-23
339 | 339 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Start Minute 0-59
340 | 340 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Stop Hour 0-23
341 | 341 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekday_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekday Stop Minute 0-59
342 | 342 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Start Hour 0-23
343 | 343 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Start Minute 0-59
344 | 344 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Stop Hour 0-23
345 | 345 | 1 | R/W | OutBack_Grid_Use_Interval_1_Weekend_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 1 Weekend Stop Minute 0-59
346 | 346 | 1 | R/W | OutBack_Grid_Use_Interval_2_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
347 | 347 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Start Hour 0-23
348 | 348 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Start Minute 0-59
349 | 349 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Stop Hour 0-23
350 | 350 | 1 | R/W | OutBack_Grid_Use_Interval_2_Weekday_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 2 Weekday Stop Minute 0-59
351 | 351 | 1 | R/W | OutBack_Grid_Use_Interval_3_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
352 | 352 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Start_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Start Hour 0-23
353 | 353 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Start_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Start Minute 0-59
354 | 354 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Stop_Hour | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Stop Hour 0-23
355 | 355 | 1 | R/W | OutBack_Grid_Use_Interval_3_Weekday_Stop_Minute | uint16 | Hour | N/A | Programmable | Grid Use Interval 3 Weekday Stop Minute 0-59
356 | 356 | 1 | R/W | OutBack_Load_Grid_Transfer_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
357 | 357 | 1 | R/W | OutBack_Load_Grid_Transfer_Threshold | uint16 | kWatts | OutBack_Voltage_SF | Programmable | Load Grid Transfer Threshold kW
358 | 358 | 1 | R/W | OutBack_Load_Grid_Transfer_Connect_Delay | uint16 | Seconds | N/A | Programmable | Load Grid Transfer Connect Delay Seconds
359 | 359 | 1 | R/W | OutBack_Load_Grid_Transfer_Disconnect_Delay | uint16 | Seconds | N/A | Programmable | Load Grid Transfer Disconnect Delay Seconds
360 | 360 | 1 | R/W | OutBack_Load_Grid_Transfer_Connect_Battery_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Load Grid Transfer Low Battery Connect Voltage
361 | 361 | 1 | R/W | OutBack_Load_Grid_Transfer_Re_Connect_Battery_Voltage | uint16 | Volts | OutBack_Voltage_SF | Programmable | Load Grid Transfer Low Battery Re-Connect Voltage
362 | 362 | 1 | R/W | OutBack_Global_Charger_Control_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
363 | 363 | 1 | R/W | OutBack_Global_Charger_Control_Output_Limit | uint16 | Amps | N/A | Programmable | Global Charger Output Limit Amps
364 | 364 | 1 | R/W | OutBack_Radian_AC_Coupled_Control_Mode | uint16 | Enumerated | N/A | Programmable | 0=Disabled, 1=Enabled
365 | 365 | 1 | R/W | OutBack_Radian_AC_Coupled_AUX_Port | uint16 | Port | N/A | Programmable | Radian Inverter Port Number for AUX Control 0-10
366 | 367 | 2 | W | OutBack_URL_Update_Lock | uint32 | key | N/A | Write Only | Unlock Key
368 | 387 | 20 | R/W | OutBack_Web_Reporting_Base_URL | string (40) | N/A | N/A | Programmable | WEB Reporting Base URL
388 | 388 | 1 | R/W | OutBack_WEB_User_Logged_In_Status | uint16 | Enumerated | N/A | Programmable | 0=WEB User NOT logged in, 1=WEB user logged in
389 | 389 | 1 | R | OutBack_HUB_Type | uint16 | Enumerated | N/A | Read Only | 0=Legecy HUB, 4= HUB4, 10=HUB10.3, 11=HUB3PH
390 | 390 | 1 | R | OutBack_HUB_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | HUB Major firmware revision
391 | 391 | 1 | R | OutBack_HUB_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | HUB Mid firmware revision
392 | 392 | 1 | R | OutBack_HUB_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | HUB Minor firmware revision
393 | 393 | 1 | R/W | OutBack_Year | uint16 | N/A | N/A | Programmable | Clock year (4 digit)
394 | 394 | 1 | R/W | Outback_Month | uint16 | N/A | N/A | Programmable | Clock Month (1 - 12)
395 | 395 | 1 | R/W | OutBack_Day | uint16 | N/A | N/A | Programmable | Clock Day (1 - 31)
396 | 396 | 1 | R/W | OutBack_Hour | uint16 | N/A | N/A | Programmable | Clock Hour (0 - 23)
397 | 397 | 1 | R/W | Outback_Minute | uint16 | N/A | N/A | Programmable | Clock Minute (0 - 59)
398 | 398 | 1 | R/W | OutBack_Second | uint16 | N/A | N/A | Programmable | Clock Second (0 - 59)
399 | 399 | 1 | R | OutBack_Temp_Batt | int16 | Degrees C | N/A | Measured | Battery temp in degrees C
400 | 400 | 1 | R | OutBack_Temp_Ambient | int16 | Degrees C | N/A | Measured | Ambient temp from temp sensor connected to device, in degrees C
401 | 401 | 1 | R | OutBack_Temp_SF | int16 | N/A | N/A | 0 | Temperature Scale Factor
402 | 402 | 1 | R | OutBack_Error | uint16 | Bitfield | N/A | Read Only | Bit field for errors. See Outback_Error Table
403 | 403 | 1 | R | OutBack_Status | uint16 | Bitfield | N/A | Read Only | Bit field for status.See Outback_Status Table
404 | 404 | 1 | R/W | OutBack_Update_Device_Firmware_Port | uint16 | Bitfield | N/A | Programmable | Device Firmware update See Device_FW_Update
405 | 405 | 1 | R | OutBack_Gateway_Type | uint16 | Enumerated | N/A | Read Only | 1=AXS Port, 2= MATE3
406 | 406 | 1 | R | OutBack_System_Voltage | uint16 | Volts | N/A | Read Only | 12, 24, 26, 48 or 60 VDC
407 | 407 | 1 | R | OutBack_Measured_System_Voltage | uint16 | Volts | OutBack_Voltage_SF | Read Only | Current system battery voltage computed by gateway
Outback_Error Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | High limit last write
[8 empty] | 0x0002 | Low limit last write
[8 empty] | 0x0004 | Last write invalid
[8 empty] | 0x0008 | DHCP failed
[8 empty] | 0x0010 | DNS resolve failure
[8 empty] | 0x0020 | SMTP authorization failed
[8 empty] | 0x0040 | SMTP send failed
[8 empty] | 0x0080 | FTP Error
[8 empty] | 0x0100 | SD-Card Error
[8 empty] | 0x0200 | SNTP failure
[8 empty] | 0x0400 | Write while locked
[8 empty] | 0x0800 | Device firmware updating not supported
[8 empty] | 0x1000 | Device firmware update file not found
[8 empty] | 0x2000 | Device firmware update file invalid
[8 empty] | 0x4000 | Device firmware update failure
Table 2 Charge Controller Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | CC_DID | uint16 | N/A | N/A | 64111 | Uniquely identifies this as a SunSpec Basic Charge Controller
2 | 2 | 1 | R | CC_Length | uint16 | Registers | N/A | 26 | Length of block in 16-bit registers
3 | 3 | 1 | R | CC_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
4 | 4 | 1 | R | CC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | CC_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
6 | 6 | 1 | R | CC_Power_SF | int16 | N/A | N/A | 0 | DC Power Scale Factor
7 | 7 | 1 | R | CC_AH_SF | int16 | N/A | N/A | 0 | DC Amp Hours Scale Factor
8 | 8 | 1 | R | CC_KWH_SF | int16 | N/A | N/A | -1 | DC kWH Scale Factor
9 | 9 | 1 | R | CC_Batt_Voltage | uint16 | Volts | CC_Voltage_SF | Measured | Battery Voltage
10 | 10 | 1 | R | CC_Array_Voltage | uint16 | Volts | CC_Voltage_SF | Measured | DC Source Voltage
11 | 11 | 1 | R | CC_Batt_Current | uint16 | Amps | CC_Current_SF | Measured | Battery Current
12 | 12 | 1 | R | CC_Array_Current | uint16 | Amps | CC_Power_SF | Measured | DC Source Current
13 | 13 | 1 | R | CC_Charger_State | uint16 | Enumerated | N/A | N/A | 0 = Silent; 1 = Float; 2 = Bulk; 3 = Absorb; 4 = EQ
14 | 14 | 1 | R | CC_Watts | uint16 | Watts | CC_Power_SF | Measured | CC Wattage Output
15 | 15 | 1 | R | CC_Todays_Min_Battery_Volts | uint16 | Volts | CC_Voltage_SF | Measured | Minimum Voltage for battery today
16 | 16 | 1 | R | CC_Todays_Max_Battery_Volts | uint16 | Volts | CC_Voltage_SF | Measured | Maximum Voltage for battery today
17 | 17 | 1 | R | CC_VOC | uint16 | Volts | CC_Voltage_SF | Measured | Last Open Circuit Voltage (array)
18 | 18 | 1 | R | CC_Todays_Peak_VOC | uint16 | Volts | N/A | Measured | Highest VOC today
19 | 19 | 1 | R | CC_Todays_kWH | uint16 | KWH | CC_KWH_SF | Measured | Daily accumulated Kwatt hours output
20 | 20 | 1 | R | CC_Todays_AH | uint16 | AH | CC_AH_SF | Measured | Daily accumulated amp hours output
21 | 21 | 1 | R | CC_Lifetime_kWH_Hours | uint16 | KWH | N/A | Measured | Lifetime Total Kwatt Hours
22 | 22 | 1 | R | CC_Lifetime_kAmp_Hours | uint16 | Amps | CC_KWH_SF | Measured | Lifetime Total K-Amp Hours
23 | 23 | 1 | R | CC_Lifetime_Max_Watts | uint16 | Watts | CC_Power_SF | Measured | Lifetime Maximum Wattage
24 | 24 | 1 | R | CC_Lifetime_Max_Battery_Volts | uint16 | Volts | CC_Voltage_SF | Measured | Lifetime Maximum Battery Voltage
25 | 25 | 1 | R | CC_Lifetime_Max_VOC | uint16 | Volts | CC_Voltage_SF | Measured | Lifetime Maximum VOC
26 | 26 | 1 | R | CC_Temp_SF | uint16 | N/A | N/A | 0 | FM80 Extreme Temperature scale factor
27 | 27 | 1 | R | CC_Temp_Output_FETs | int16 | Degrees C | CC_Power_SF | Measured | FM80 Extreme Output FET Temperature
28 | 28 | 1 | R | CC_Temp_Enclosure | int16 | Degrees C | CC_Power_SF | Measured | FM80 Extreme Enclosure Temperature
Table 3 Charge Controller Configuration Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | CCconfig_DID | uint16 | N/A | N/A | 64112 | Vendor Extension for OutBack FM Series Charge Controllers
2 | 2 | 1 | R | CCconfig_Length | uint16 | Registers | N/A | 88 | Length of block in 16-bit registers
3 | 3 | 1 | R | CCconfig_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
4 | 4 | 1 | R | CCconfig_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | CCconfig_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
6 | 6 | 1 | R | CCconfig_Hours_SF | int16 | N/A | N/A | -1 | Time in Hours Scale Factor
7 | 7 | 1 | R | CCconfig_Power_SF | int16 | N/A | N/A | 0 | Power Scale Factor
8 | 8 | 1 | R | CCconfig_AH_SF | int16 | N/A | N/A | 0 | Amp Hours Scale Factor
9 | 9 | 1 | R | CCconfig_KWH_SF | int16 | N/A | N/A | -1 | DC kWH Scale Factor
10 | 10 | 1 | R | CCconfig_Faults | uint16 | Bitfield | N/A | N/A | CC Error Flags: 0x0080=High VOC, 0x0040=Over Temp, 0x0020=Shorted Battery Temp Sensor, 0x0010=Fault Input Active
11 | 11 | 1 | R/W | CCconfig_Absorb_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Absorb Voltage Target
12 | 12 | 1 | R/W | CCconfig_Absorb_Time_Hours | uint16 | Hours | CCconfig_Hours_SF | Programmable | Absorb Time Hours
13 | 13 | 1 | R/W | CCconfig_Absorb_End_Amps | uint16 | Amps | N/A | Programmable | Amperage to end Absorbing
14 | 14 | 1 | R/W | CCconfig_Rebulk_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Voltage to re-initiate Bulk charge
15 | 15 | 1 | R/W | CCconfig_Float_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Float Voltage Target
16 | 16 | 1 | R/W | CCconfig_Bulk_Current | uint16 | Amps | CCconfig_Current_SF | Programmable | Max Output Current Limit
17 | 17 | 1 | R/W | CCconfig_EQ_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Target Voltage for Equalize
18 | 18 | 1 | R/W | CCconfig_EQ_Time_Hours | uint16 | Hours | N/A | Programmable | EQ Time Hours
19 | 19 | 1 | R/W | CCconfig_Auto_EQ_Days | uint16 | Days | N/A | Programmable | Auto EQ Interval Days
20 | 20 | 1 | R/W | CCconfig_MPPT_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Auto; 1 = U-Pick
21 | 21 | 1 | R/W | CCconfig_Sweep_Width | uint16 | Enumerated | N/A | Programmable | 0 = Full; 1 = Half
22 | 22 | 1 | R/W | CCconfig_Sweep_Max_Percentage | uint16 | Enumerated | N/A | Programmable | 0 = 80; 1 = 85; 2 = 90; 3 = 99
23 | 23 | 1 | R/W | CCconfig_U_Pick_PWM_Duty_Cycle | uint16 | Percentage | CCconfig_Voltage_SF | Programmable | Park Duty Cycle (%) (40% - 90%)
24 | 24 | 1 | R/W | CCconfig_Grid_Tie_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Grid Tie Mode disabled; 1 = Grid Tie Mode enabled
25 | 25 | 1 | R/W | CCconfig_Temp_Comp_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Wide; 1 = User Limited
26 | 26 | 1 | R/W | CCconfig_Temp_Comp_Lower_Limit_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | RTS compensation lower voltage limit
27 | 27 | 1 | R/W | CCconfig_Temp_Comp_Upper_Limit_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | RTS compensation upper voltage limit
28 | 28 | 1 | R/W | CCconfig_Temp_Comp_Slope | uint16 | Milli Volts | N/A | Programmable | RTS temp compensation Slope 2-6 mV per Degree C
29 | 29 | 1 | R/W | CCconfig_Auto_Restart_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Restart every 90 minutes; 2 = Restart every 90 minutes if absorb charging or float charging
30 | 30 | 1 | R/W | CCconfig_Wakeup_VOC | uint16 | Volts | CCconfig_Voltage_SF | Programmable | VOC change which causes Wakeup occurs
31 | 31 | 1 | R/W | CCconfig_Snooze_Mode_Amps | uint16 | Amps | CCconfig_Voltage_SF | Programmable | Snooze Mode Amps
32 | 32 | 1 | R/W | CCconfig_Wakeup_Interval | uint16 | Mins | N/A | Programmable | How often to check for Wakeup condition
33 | 33 | 1 | R/W | CCconfig_AUX_Mode | uint16 | Enumerated | N/A | Programmable | 0 = Float; 1 = Diversion: Relay; 2 = Diversion: Solid St; 3 = Low Batt Disconnect; 4 = Remote; 5 = Vent Fan; 6 = PV Trigger; 7 = Error Output; 8 = Night Light
34 | 34 | 1 | R/W | CCconfig_AUX_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Auto; 2 = On
35 | 35 | 1 | R | CCconfig_AUX_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
36 | 36 | 1 | R/W | CCconfig_AUX_Polarity | uint16 | Enumerated | N/A | Programmable | 0 = Low; 1 = High
37 | 37 | 1 | R/W | CCconfig_AUX_Low_Batt_Disconnect | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Low Battery Disconnect Voltage
38 | 38 | 1 | R/W | CCconfig_AUX_Low_Batt_Reconnect | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Low Battery Reconnect Volts
39 | 39 | 1 | R/W | CCconfig_AUX_Low_Batt_Disconnect_Delay | uint16 | Secs | N/A | Programmable | Low Battery Disconnect Delay (secs)
40 | 40 | 1 | R/W | CCconfig_AUX_Vent_Fan_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Vent Fan Voltage
41 | 41 | 1 | R/W | CCconfig_AUX_PV_Limit_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Voltage at which PV disconnect occurs
42 | 42 | 1 | R/W | CCconfig_AUX_PV_Limit_Hold_Time | uint16 | Secs | CCconfig_Hours_SF | Programmable | AUX PV Trigger Hold Time
43 | 43 | 1 | R/W | CCconfig_AUX_Night_Light_Thres_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Voltage Threshold for AUX Night Light
44 | 44 | 1 | R/W | CCconfig_Night_Light_ON_Hours | uint16 | Hours | N/A | Programmable | Night Light ON Time
45 | 45 | 1 | R/W | CCconfig_Night_Light_ON_Hyst_Time | uint16 | Mins | N/A | Programmable | Night Light ON Hyst Time
46 | 46 | 1 | R/W | CCconfig_Night_Light_OFF_Hyst_Time | uint16 | Mins | N/A | Programmable | Night Light OFF Hyst Time
47 | 47 | 1 | R/W | CCconfig_AUX_Error_Battery_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | Battery voltage at which Aux Error occurs
48 | 48 | 1 | R/W | CCconfig_AUX_Divert_Hold_Time | uint16 | Seconds | CCconfig_Hours_SF | Programmable | AUX Diver Hold Time
49 | 49 | 1 | R/W | CCconfig_AUX_Divert_Delay_Time | uint16 | Secs | N/A | Programmable | AUX Divert Delay
50 | 50 | 1 | R/W | CCconfig_AUX_Divert_Relative_Volts | int16 | Volts | CCconfig_Voltage_SF | Programmable | AUX Divert Relative Volts
51 | 51 | 1 | R/W | CCconfig_AUX_Divert_Hyst_Volts | uint16 | Volts | CCconfig_Voltage_SF | Programmable | AUX Divert Hyst Volts
52 | 52 | 1 | R | CCconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | Charge Controller Major firmware revision
53 | 53 | 1 | R | CCconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | Charge Controller Mid firmware revision
54 | 54 | 1 | R | CCconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | Charge Controller Minor firmware revision
55 | 55 | 1 | R/W | CCconfig_Set_Data_Log_Day_Offset | uint16 | Days | N/A | Programmable | Day offset 0-128, 0 =Today, 1 = -1 day …
56 | 56 | 1 | R | CCconfig_Get_Current_Data_Log_Day_Offset | uint16 | Days | N/A | Read Only | Current Data Log Day Offset
57 | 57 | 1 | R | CCconfig_Data_Log_Daily_AH | uint16 | AH | CCconfig_AH_SF | Read Only | Data Log AH
58 | 58 | 1 | R | CCconfig_Data_Log_Daily_kWH | uint16 | KWH | CCconfig_KWH_SF | Read Only | Data Log kWH
59 | 59 | 1 | R | CCconfig_Data_Log_Daily_Max_Output_Amps | uint16 | Amps | CCconfig_Voltage_SF | Read Only | Data Log maximum Output Amps
60 | 60 | 1 | R | CCconfig_Data_Log_Daily_Max_Output_Watts | uint16 | Watts | CCconfig_Power_SF | Read Only | Data Log maximum Output Wattage
61 | 61 | 1 | R | CCconfig_Data_Log_Daily_Absorb_Time | uint16 | Mins | N/A | Read Only | Data Log Absorb Time Minutes
62 | 62 | 1 | R | CCconfig_Data_Log_Daily_Float_Time | uint16 | Mins | N/A | Read Only | Data Log Float Time Minutes
63 | 63 | 1 | R | CCconfig_Data_Log_Daily_Min_Batt_Volts | uint16 | Volts | CCconfig_Voltage_SF | Read Only | Data Log minimum daily battery voltage
64 | 64 | 1 | R | CCconfig_Data_Log_Daily_Max_Batt_Volts | uint16 | Volts | CCconfig_Voltage_SF | Read Only | Data Log maximum daily battery voltage
65 | 65 | 1 | R | CCconfig_Data_Log_Daily_Max_Input_Volts | uint16 | Volts | N/A | Read Only | Data Log maximum daily input voltage
66 | 66 | 1 | R | CCconfig_Clear_Data_Log_Read | uint16 | N/A | N/A | Read Only | Read value needed to clear data log
67 | 67 | 1 | W | CCconfig_Clear_Data_Log_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear data log
68 | 68 | 1 | R | CCconfig_Stats_Maximum_Reset_Read | uint16 | N/A | N/A | Read Only | Read value needed to clear Stats Maximums
69 | 69 | 1 | W | CCconfig_Stats_Maximum_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear Stats Maximums
70 | 70 | 1 | R | CCconfig_Stats_Totals_Reset_Read | uint16 | N/A | N/A | Read Only | Read value nneded to clear Stats Totals
71 | 71 | 1 | W | CCconfig_Stats_Totals_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear Stats Totals
72 | 72 | 1 | R/W | CCconfig_Battery_Voltage_Calibrate_Offset | int16 | DC Volts | CCconfig_Voltage_SF | Programmable | Battery voltage calibration offset
73 | 81 | 9 | R | CCconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
82 | 90 | 9 | R | CCconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
Table 4 Split Phase Radian Inverter Real Time Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | GS_Split_DID | uint16 | N/A | N/A | 64115 | Vendor Extension for OutBack Radian Series Split Phase Inverter Status Block
2 | 2 | 1 | R | GS_Split_Length | uint16 | Registers | N/A | 51 | Length of block in 16-bit registers
3 | 3 | 1 | R | GS_Split_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
4 | 4 | 1 | R | GS_Split_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | GS_Split_AC_Current_SF | int16 | N/A | N/A | 0 | AC Current Scale Factor
6 | 6 | 1 | R | GS_Split_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
7 | 7 | 1 | R | GS_Split_AC_Frequency_SF | int16 | N/A | N/A | -1 | AC Frequency Scale Factor
8 | 8 | 1 | R | GS_Split_L1_Inverter_Output_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter output current
9 | 9 | 1 | R | GS_Split_L1_Inverter_Charge_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter charger current
10 | 10 | 1 | R | GS_Split_L1_Inverter_Buy_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter buy current
11 | 11 | 1 | R | GS_Split_L1_Inverter_Sell_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L1 inverter sell current
12 | 12 | 1 | R | GS_Split_L1_Grid_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L1 Grid Input AC Voltage
13 | 13 | 1 | R | GS_Split_L1_Gen_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L1 Gen Input AC Voltage
14 | 14 | 1 | R | GS_Split_L1_Output_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L1 Output AC Voltage
15 | 15 | 1 | R | GS_Split_L2_Inverter_Output_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter output current
16 | 16 | 1 | R | GS_Split_L2_Inverter_Charge_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter charger current
17 | 17 | 1 | R | GS_Split_L2_Inverter_Buy_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter buy current
18 | 18 | 1 | R | GS_Split_L2_Inverter_Sell_Current | int16 | Amps | GS_Split_AC_Current_SF | Measured | L2 inverter sell current
19 | 19 | 1 | R | GS_Split_L2_Grid_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L2 Grid Input AC Voltage
20 | 20 | 1 | R | GS_Split_L2_Gen_Input_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L2 Gen Input AC Voltage
21 | 21 | 1 | R | GS_Split_L2_Output_AC_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | L2 Output AC Voltage
22 | 22 | 1 | R | GS_Split_Inverter_Operating_mode | int16 | Enumerated | N/A | Read Only | 0=Off, 1=Searching, 2=Inverting, 3=Charging, 4=Silent, 5=Float, 6=EQ, 7=Charger Off, 8=Support, 9=Selling, 10=Pass through, 14=Offsetting
23 | 23 | 1 | R | GS_Split_Error_Flags | int16 | Bitfield | N/A | N/A | Bit field for errors. See GS_Error table
24 | 24 | 1 | R | GS_Split_Warning_Flags | int16 | Bitfield | N/A | N/A | Bit field for warnings See GS_Warning table
25 | 25 | 1 | R | GS_Split_Battery_Voltage | int16 | Volts DC | GS_Split_DC_Voltage_SF | Measured | Battery Voltage
26 | 26 | 1 | R | GS_Split_Temp_Compensated_Target_Voltage | int16 | Volts DC | GS_Split_DC_Voltage_SF | Read Only | Temperature compensated target battery voltage
27 | 27 | 1 | R | GS_Split_AUX_Output_State | int16 | Enumerated | N/A | N/A | 0 = Disabled; 1 = Enabled
28 | 28 | 1 | R | GS_Split_AUX_Relay_Output_State | int16 | Enumerated | N/A | N/A | 0 = Disabled; 1 = Enabled
29 | 29 | 1 | R | GS_Split_L_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Left module transformer temp in degrees C
30 | 30 | 1 | R | GS_Split_L_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Left module capacitor temp in degrees C
31 | 31 | 1 | R | GS_Split_L_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Left module FET temp in degrees C
32 | 32 | 1 | R | GS_Split_R_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Right module transformer temp in degrees C
33 | 33 | 1 | R | GS_Split_R_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Right module capacitor temp in degrees C
34 | 34 | 1 | R | GS_Split_R_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Right module FET temp in degrees C
35 | 35 | 1 | R | GS_Split_Battery_Temperature | int16 | Degrees C | N/A | Measured | Battery temp in degrees C
36 | 36 | 1 | R | GS_Split_AC_Input_Selection | int16 | Enumerated | N/A | Read Only | 0=Grid, 1=Gen
37 | 37 | 1 | R | GS_Split_AC_Input_Frequency | int16 | Hz | GS_Split_AC_Frequency_SF | Measured | Selected AC Input frequency HZ
38 | 38 | 1 | R | GS_Split_AC_Input_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Measured | Selected Input AC Voltage
39 | 39 | 1 | R | GS_Split_AC_Input_State | int16 | Enumerated | N/A | N/A | 1=AC Use, 0=AC_Drop
40 | 40 | 1 | R | GS_Split_Minimum_AC_Input_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Read Only | Minimum Input AC Voltage (Write to clear stored value)
41 | 41 | 1 | R | GS_Split_Maximum_AC_Input_Voltage | int16 | Volts AC | GS_Split_AC_Voltage_SF | Read Only | Maximum Input AC Voltage (Write to clear stored value)
42 | 42 | 1 | R | GS_Split_Sell_Status | int16 | Bitfield | N/A | N/A | Bit field for sell status See GS_Sell_Status table
43 | 43 | 1 | R | GS_Split_kWh_SF | int16 | N/A | N/A | -1 | AC kWh scale factor
44 | 44 | 1 | R | GS_Split_AC1_L1_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Buy L1 kWh
45 | 45 | 1 | R | GS_Split_AC2_L1_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC2 Buy L1 kWh
46 | 46 | 1 | R | GS_Split_AC1_L1_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Sell L1 kWh
47 | 47 | 1 | R | GS_Split_AC2_L1_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC2 Sell L1 kWh
48 | 48 | 1 | R | GS_Split_L1_Output_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily Output L1 kWh
49 | 49 | 1 | R | GS_Split_AC1_L2_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Buy L2 kWh
50 | 50 | 1 | R | GS_Split_AC2_L2_Buy_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Sell L2 kWh
51 | 51 | 1 | R | GS_Split_AC1_L2_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC1 Sell L2 kWh
52 | 52 | 1 | R | GS_Split_AC2_L2_Sell_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily AC2 Sell L2 kWh
53 | 53 | 1 | R | GS_Split_L2_Output_kWh | uint16 | kWh | GS_Split_kWh_SF | Measured | Daily Output L2 kWh
GS_Error Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | Low AC output voltage
[8 empty] | 0x0002 | Stacking error
[8 empty] | 0x0004 | Over temperature error
[8 empty] | 0x0008 | Low battery voltage
[8 empty] | 0x0010 | Phase loss
[8 empty] | 0x0020 | High battery voltage
[8 empty] | 0x0040 | AC output shorted
[8 empty] | 0x0080 | AC backfeed
GS_Warning Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | AC input frequency too high
[8 empty] | 0x0002 | AC input frequency too low
[8 empty] | 0x0004 | AC input voltage too low
[8 empty] | 0x0008 | AC input voltage too high
[8 empty] | 0x0010 | AC input current exceeds max
[8 empty] | 0x0020 | Temperature sensor bad
[8 empty] | 0x0040 | Communications error
[8 empty] | 0x0080 | Cooling fan fault
GS_Sell_Status Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | AC input frequency too high
[8 empty] | 0x0002 | AC input frequency too low
[8 empty] | 0x0004 | AC input voltage too low
[8 empty] | 0x0008 | AC input voltage too high
[8 empty] | 0x0010 | Awaiting sell delay
[8 empty] | 0x0020 | Sell disabled
[8 empty] | 0x0040 | Battery voltage less than target
Table 5 Radian Inverter Configuration Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | GSconfig_DID | uint16 | N/A | N/A | 64116 | Vendor Extension for OutBack Radian Series Split Phase Inverter Configuration Block
2 | 2 | 1 | R | GSconfig_Length | uint16 | Registers | N/A | 82 | Length of block in 16-bit registers
3 | 3 | 1 | R | GSconfig_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
4 | 4 | 1 | R | GSconfig_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | GSconfig_AC_Current_SF | int16 | N/A | N/A | -1 | AC Current Scale Factor
6 | 6 | 1 | R | GSconfig_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
7 | 7 | 1 | R | GSconfig_Time_SF | int16 | N/A | N/A | -1 | Time Scale Factor
8 | 8 | 1 | R | GSconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Major firmware revision
9 | 9 | 1 | R | GSconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Mid firmware revision
10 | 10 | 1 | R | GSconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Minor firmware revision
11 | 11 | 1 | R/W | GSconfig_Absorb_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Absorb Voltage Target
12 | 12 | 1 | R/W | GSconfig_Absorb_Time_Hours | uint16 | Hours | GSconfig_Time_SF | Programmable | Absorb Time Hours
13 | 13 | 1 | R/W | GSconfig_Float_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Float Voltage Target
14 | 14 | 1 | R/W | GSconfig_Float_Time_Hours | uint16 | Hours | GSconfig_Time_SF | Programmable | Float Time Hours
15 | 15 | 1 | R/W | GSconfig_ReFloat_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | ReFloat Voltage Target
16 | 16 | 1 | R/W | GSconfig_EQ_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | EQ Voltage Target
17 | 17 | 1 | R/W | GSconfig_EQ_Time_Hours | uint16 | Hours | GSconfig_Time_SF | Programmable | EQ Time Hours
18 | 18 | 1 | R/W | GSconfig_Search_Sensitivity | uint16 | N/A | N/A | Programmable | Search sensitivity
19 | 19 | 1 | R/W | GSconfig_Search_Pulse_Length | uint16 | Cycles | N/A | Programmable | Search pulse length
20 | 20 | 1 | R/W | GSconfig_Search_Pulse_Spacing | uint16 | Cycles | N/A | Programmable | Search pulse spacing
21 | 21 | 1 | R/W | GSconfig_AC_Input_Select_Priority | uint16 | Enumerated | N/A | Programmable | 0=Grid, 1=Gen
22 | 22 | 1 | R/W | GSconfig_Grid_AC_Input_Current_Limit | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Grid AC input current limit
23 | 23 | 1 | R/W | GSconfig_Gen_AC_Input_Current_Limit | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Gen AC input current limit
24 | 24 | 1 | R/W | GSconfig_Charger_AC_Input_Current_Limit | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Charger AC input current limit
25 | 25 | 1 | R/W | GSconfig_Charger_Operating_Mode | uint16 | Enumerated | N/A | Programmable | 0=All Inverter Charging Disabled, 1=Bulk and Float Charging Enabled
26 | 26 | 1 | R/W | GSconfig_AC_Coupled | uint16 | Enumerated | N/A | Programmable | 0=No, 1=Yes (not implemented)
27 | 27 | 1 | R/W | GSconfig_Grid_Input_Mode | uint16 | Enumerated | N/A | Programmable | Grid Input Mode: 0=Generator, 1=Support, 2=Grid Tied, 3=UPS, 4=Backup, 5=Mini Grid, 6=Grid Zero
28 | 28 | 1 | R/W | GSconfig_Grid_Lower_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage lower limit
29 | 29 | 1 | R/W | GSconfig_Grid_Upper_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage upper limit
30 | 30 | 1 | R/W | GSconfig_Grid_Transfer_Delay | uint16 | msecs | N/A | Programmable | Grid Input AC transfer delay
31 | 31 | 1 | R/W | GSconfig_Grid_Connect_Delay | uint16 | Minutes | GSconfig_Time_SF | Programmable | Grid Input AC connect delay
32 | 32 | 1 | R/W | GSconfig_Gen_Input_Mode | uint16 | Enumerated | N/A | Programmable | Grid Input Mode: 0=Generator, 1=Support, 2=Grid Tied, 3=UPS, 4=Backup, 5=Mini Grid, 6=Grid Zero
33 | 33 | 1 | R/W | GSconfig_Gen_Lower_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage lower limit
34 | 34 | 1 | R/W | GSconfig_Gen_Upper_Input_Voltage_Limit | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage upper limit
35 | 35 | 1 | R/W | GSconfig_Gen_Transfer_Delay | uint16 | msecs | N/A | Programmable | Gen Input AC transfer delay
36 | 36 | 1 | R/W | GSconfig_Gen_Connect_Delay | uint16 | Minutes | GSconfig_Time_SF | Programmable | Gen Input AC connect delay
37 | 37 | 1 | R/W | GSconfig_AC_Output_Voltage | uint16 | Volts AC | GSconfig_AC_Voltage_SF | Programmable | AC output Voltage
38 | 38 | 1 | R/W | GSconfig_Low_Battery_Cut_Out_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Battery cut-out voltage
39 | 39 | 1 | R/W | GSconfig_Low_Battery_Cut_In_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Battery cut-in voltage
40 | 40 | 1 | R/W | GSconfig_AUX_Mode | uint16 | Enumerated | N/A | Programmable | 1=Load Shed, 2=Gen Alert, 3=Fault, 4=Vent Fan, 5=Cool Fan, 6=DC Divert, 7=Grid Limit/IEEE ,8=AC Source Status,9=AC Divert
41 | 41 | 1 | R/W | GSconfig_AUX_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = On; 2 = Auto
42 | 42 | 1 | R/W | GSconfig_AUX_ON_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX ON battery voltage
43 | 43 | 1 | R/W | GSconfig_AUX_ON_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX ON Delay
44 | 44 | 1 | R/W | GSconfig_AUX_OFF_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX OFF battery voltage
45 | 45 | 1 | R/W | GSconfig_AUX_OFF_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX OFF Delay
46 | 46 | 1 | R/W | GSconfig_AUX_Relay_Mode | uint16 | Enumerated | N/A | Programmable | 1=Load Shed, 2=Gen Alert, 3=Fault, 4=Vent Fan, 5=Cool Fan, 6=DC Divert, 7=Grid Limit/IEEE ,8=AC Source Status,9=AC Divert
47 | 47 | 1 | R/W | GSconfig_AUX_Relay_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = On; 2 = Auto
48 | 48 | 1 | R/W | GSconfig_AUX_Relay_ON_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX Relay ON battery voltage
49 | 49 | 1 | R/W | GSconfig_AUX_Relay_ON_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX Relay ON Delay
50 | 50 | 1 | R/W | GSconfig_AUX_Relay_OFF_Battery_Voltage | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | AUX Relay OFF battery voltage
51 | 51 | 1 | R/W | GSconfig_AUX_Relay_OFF_Delay_Time | uint16 | Minutes | GSconfig_Time_SF | Programmable | AUX Relay OFF Delay
52 | 52 | 1 | R | GSconfig_Stacking_Mode | uint16 | Enumerated | N/A | Read Only | 10=Master, 12=Slave, 17=B Phase Master, 18=C Phase Master
53 | 53 | 1 | R/W | GSconfig_Master_Power_Save_Level | uint16 | N/A | N/A | Programmable | Master inverter power save level
54 | 54 | 1 | R/W | GSconfig_Slave_Power_Save_Level | uint16 | N/A | N/A | Programmable | Slave inverter power save level
55 | 55 | 1 | R/W | GSconfig_Sell_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Sell Voltage Target
56 | 56 | 1 | R/W | GSconfig_Grid_Tie_Window | uint16 | Enumerated | N/A | Programmable | 0=IEEE, 1=User (GS8048 Only)
57 | 57 | 1 | R/W | GSconfig_Grid_Tie_Enable | uint16 | Enumerated | N/A | Programmable | 1=Yes, 0=No
58 | 58 | 1 | R/W | GSconfig_Grid_AC_Input_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | Grid AC input voltage calibration factor
59 | 59 | 1 | R/W | GSconfig_Gen_AC_Input_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | Gen AC input voltage calibration factor
60 | 59 | 1 | R/W | GSconfig_AC_Output_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | AC output voltage calibration factor
61 | 60 | 1 | R/W | GSconfig_Battery_Voltage_Calibrate_Factor | int16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Battery voltage calibration factor
62 | 61 | 1 | R/W | GSconfig_ReBulk_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | ReBulk Voltage Target
63 | 62 | 1 | R/W | GSconfig_Mini_Grid_LBX_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Mini Grid LBX reconnect to Grid Battery Voltage
64 | 63 | 1 | R/W | GSconfig_Mini_Grid_LBX_Delay | uint16 | Hours | N/A | Programmable | Mini Grid LBX reconnect to Grid Delay Time
65 | 64 | 1 | R/W | GSconfig_Grid_Zero_DoD_Volts | uint16 | DC Volts | GSconfig_DC_Voltage_SF | Programmable | Grid Zero DoD Voltage
66 | 65 | 1 | R/W | GSconfig_Grid_Zero_DoD_Max_Offset_AC_Amps | uint16 | Amps | GSconfig_AC_Current_SF | Programmable | Grid Zero Maximum Offset AC Amps
67 | 75 | 9 | R | GSconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
76 | 84 | 9 | R | GSconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
Table 6 Single Phase Radian Inverter Real Time Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | GS_Single_DID | uint16 | N/A | N/A | 64117 | Vendor Extension for OutBack Radian Series Split Phase Inverter Status Block
2 | 2 | 1 | R | GS_Single_Length | uint16 | Registers | N/A | 39 | Length of block in 16-bit registers
3 | 3 | 1 | R | GS_Single_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
4 | 4 | 1 | R | GS_Single_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | GS_Single_AC_Current_SF | int16 | N/A | N/A | 0 | AC Current Scale Factor
6 | 6 | 1 | R | GS_Single_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
7 | 7 | 1 | R | GS_Single_AC_Frequency_SF | int16 | N/A | N/A | -1 | AC Frequency Scale Factor
8 | 8 | 1 | R | GS_Single_Inverter_Output_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter output current
9 | 9 | 1 | R | GS_Single_Inverter_Charge_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter charger current
10 | 10 | 1 | R | GS_Single_Inverter_Buy_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter buy current
11 | 11 | 1 | R | GS_Single_Inverter_Sell_Current | uint16 | Amps | GS_Single_AC_Current_SF | Measured | Inverter sell current
12 | 12 | 1 | R | GS_Single_Grid_Input_AC_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Grid Input AC Voltage
13 | 13 | 1 | R | GS_Single_Gen_Input_AC_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Gen Input AC Voltage
14 | 14 | 1 | R | GS_Single_Output_AC_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Output AC Voltage
15 | 15 | 1 | R | GS_Single_Inverter_Operating_mode | uint16 | Enumerated | N/A | Read Only | 0=Off, 1=Searching, 2=Inverting, 3=Charging, 4=Silent, 5=Float, 6=EQ, 7=Charger Off, 8=Support, 9=Selling, 10=Pass through, 14=Offsetting
16 | 16 | 1 | R | GS_Single_Error_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for errors. See GS_Error Table
17 | 17 | 1 | R | GS_Single_Warning_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for warnings See GS_Warning Table
18 | 18 | 1 | R | GS_Single_Battery_Voltage | uint16 | Volts DC | GS_Single_DC_Voltage_SF | Measured | Battery Voltage
19 | 19 | 1 | R | GS_Single_Temp_Compensated_Target_Voltage | uint16 | Volts DC | GS_Single_DC_Voltage_SF | Read Only | Temperature compensated target battery voltage
20 | 20 | 1 | R | GS_Single_AUX_Output_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
21 | 21 | 1 | R | GS_Single_AUX_Relay_Output_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
22 | 22 | 1 | R | GS_Single_L_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Left module transformer temp in degrees C
23 | 23 | 1 | R | GS_Single_L_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Left module capacitor temp in degrees C
24 | 24 | 1 | R | GS_Single_L_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Left module FET temp in degrees C
25 | 25 | 1 | R | GS_Single_R_Module_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Right module transformer temp in degrees C
26 | 26 | 1 | R | GS_Single_R_Module_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Right module capacitor temp in degrees C
27 | 27 | 1 | R | GS_Single_R_Module_FET_Temperature | int16 | Degrees C | N/A | Measured | Right module FET temp in degrees C
28 | 28 | 1 | R | GS_Single_Battery_Temperature | uint16 | Degrees C | N/A | Measured | Battery temp in degrees C
29 | 29 | 1 | R | GS_Single_AC_Input_Selection | uint16 | Enumerated | N/A | Read Only | 0=Grid, 1=Gen
30 | 30 | 1 | R | GS_Single_AC_Input_Frequency | uint16 | Hz | GS_Single_AC_Frequency_SF | Measured | Selected AC Input frequency HZ
31 | 31 | 1 | R | GS_Single_AC_Input_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Measured | Selected Input AC Voltage
32 | 32 | 1 | R | GS_Single_AC_Input_State | uint16 | Enumerated | N/A | N/A | 1=AC Use, 0=AC_Drop
33 | 33 | 1 | R | GS_Single_Minimum_AC_Input_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Read Only | Minimum Input AC Voltage (Write to clear value)
34 | 34 | 1 | R | GS_Single_Maximum_AC_Input_Voltage | uint16 | Volts AC | GS_Single_AC_Voltage_SF | Read Only | Maximum Input AC Voltage (Write to clear value)
35 | 35 | 1 | R | GS_Single_Sell_Status | uint16 | Bitfield | N/A | N/A | Bit field for sell status See GS_Sell_Status Table
36 | 36 | 1 | R | GS_Single_kWh_SF | int16 | N/A | N/A | -1 | AC kWh scale factor
37 | 37 | 1 | R | GS_Single_AC1_Buy_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC1 Buy kWh
38 | 38 | 1 | R | GS_Single_AC2_Buy_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC2 Buy kWh
39 | 39 | 1 | R | GS_Single_AC1_Sell_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC1 Sell kWh
40 | 40 | 1 | R | GS_Single_AC2_Sell_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily AC2 Sell kWh
41 | 41 | 1 | R | GS_Single_Output_kWh | uint16 | kWh | GS_Single_kWh_SF | Measured | Daily Output kWh
Table 7 FX Inverter Real Time Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | FX_DID | uint16 | N/A | N/A | 64113 | Vendor Extension for OutBack FX Series Inverter Status Block
2 | 2 | 1 | R | FX_Length | uint16 | Registers | N/A | 29 | Length of block in 16-bit registers
3 | 3 | 1 | R | FX_Port_number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
4 | 4 | 1 | R | FX_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | FX_AC_Current_SF | int16 | N/A | N/A | 0 | AC Current Scale Factor
6 | 6 | 1 | R | FX_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
7 | 7 | 1 | R | FX_AC_Frequency_SF | int16 | N/A | N/A | -1 | AC Frequency Scale Factor
8 | 8 | 1 | R | FX_Inverter_Output_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter output current
9 | 9 | 1 | R | FX_Inverter_Charge_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter charger current
10 | 10 | 1 | R | FX_Inverter_Buy_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter buy current
11 | 11 | 1 | R | FX_Inverter_Sell_Current | uint16 | Amps | FX_AC_Current_SF | Measured | Inverter sell current
12 | 12 | 1 | R | FX_Output_AC_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Measured | Output AC Voltage
13 | 13 | 1 | R | FX_Inverter_Operating_Mode | uint16 | Enumerated | N/A | Read Only | 0=Off, 1=Searching, 2=Inverting, 3=Charging, 4=Silent, 5=Float, 6=EQ, 7=Charger Off, 8=Support, 9=Selling, 10=Pass through, 14=Offsetting
14 | 14 | 1 | R | FX_Error_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for errors. See FX_Error Table
15 | 15 | 1 | R | FX_Warning_Flags | uint16 | Bitfield | N/A | Read Only | Bit field for warnings See FX_Warning Table
16 | 16 | 1 | R | FX_Battery_Voltage | uint16 | Volts DC | FX_DC_Voltage_SF | Measured | Battery Voltage
17 | 17 | 1 | R | FX_Temp_Compensated_Target_Voltage | uint16 | Volts DC | FX_DC_Voltage_SF | Read Only | Temperature compensated target battery voltage
18 | 18 | 1 | R | FX_AUX_Output_State | uint16 | Enumerated | N/A | Read Only | 0 = Disabled; 1 = Enabled
19 | 19 | 1 | R | FX_Transformer_Temperature | int16 | Degrees C | N/A | Measured | Transformer temp in degrees C
20 | 20 | 1 | R | FX_Capacitor_Temperature | int16 | Degrees C | N/A | Measured | Capacitor temp in degrees C
21 | 21 | 1 | R | FX_FET_Temperature | int16 | Degrees C | N/A | Measured | FET temp in degrees C
22 | 22 | 1 | R | FX_AC_Input_Frequency | uint16 | Hz | FX_AC_Frequency_SF | Measured | Selected AC Input frequency HZ
23 | 23 | 1 | R | FX_AC_Input_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Measured | Selected Input AC Voltage
24 | 24 | 1 | R | FX_AC_Input_State | uint16 | Enumerated | N/A | N/A | 1=AC Use, 0=AC_Drop
25 | 25 | 1 | R | FX_Minimum_AC_Input_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Read Only | Minimum Input AC Voltage (Write to clear value)
26 | 26 | 1 | R | FX_Maximum_AC_Input_Voltage | uint16 | Volts AC | FX_AC_Voltage_SF | Read Only | Maximum Input AC Voltage (Write to clear value)
27 | 27 | 1 | R | FX_Sell_Status | uint16 | Bitfield | N/A | N/A | Bit field for sell status See FX_Sell_Status Table
28 | 28 | 1 | R | FX_kWh_SF | int16 | N/A | N/A | -1 | AC kWh scale factor
29 | 29 | 1 | R | FX_Buy_kWh | uint16 | kWh | FX_kWh_SF | Measured | Daily Buy kWh
30 | 30 | 1 | R | FX_Sell_kWh | uint16 | kWh | FX_kWh_SF | Measured | Daily Sell kWh
31 | 31 | 1 | R | FX_Output_kWh | uint16 | kWh | FX_kWh_SF | Measured | Daily Output kWh
FX_Error Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | Low AC output voltage
[8 empty] | 0x0002 | Stacking error
[8 empty] | 0x0004 | Over temperature error
[8 empty] | 0x0008 | Low battery voltage
[8 empty] | 0x0010 | Phase loss
[8 empty] | 0x0020 | High battery voltage
[8 empty] | 0x0040 | AC output shorted
[8 empty] | 0x0080 | AC backfeed
FX_Warning Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | AC input frequency too high
[8 empty] | 0x0002 | AC input frequency too low
[8 empty] | 0x0004 | AC input voltage too low
[8 empty] | 0x0008 | AC input voltage too high
[8 empty] | 0x0010 | AC input current exceeds max
[8 empty] | 0x0020 | Temperature sensor bad
[8 empty] | 0x0040 | Communications error
[8 empty] | 0x0080 | Cooling fan fault
FX_Sell_Status Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | AC input frequency too high
[8 empty] | 0x0002 | AC input frequency too low
[8 empty] | 0x0004 | AC input voltage too low
[8 empty] | 0x0008 | AC input voltage too high
[8 empty] | 0x0010 | Awaiting sell delay
[8 empty] | 0x0020 | Sell disabled
[8 empty] | 0x0040 | Battery voltage less than target
[8 empty] | 0x0080 | AC2 selected
Table 8 FX Inverter Configuration Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | FXconfig_DID | uint16 | N/A | N/A | 64114 | Vendor Extension for OutBack FX Series Inverter Configuration Block
2 | 2 | 1 | R | FXconfig_Length | uint16 | Registers | N/A | 72 | Length of block in 16-bit registers
3 | 3 | 1 | R | FXconfig_Port_Number | uint16 | N/A | N/A | 0-10 | Port number on Outback network
4 | 4 | 1 | R | FXconfig_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | FXconfig_AC_Current_SF | int16 | N/A | N/A | -1 | AC Current Scale Factor
6 | 6 | 1 | R | FXconfig_AC_Voltage_SF | int16 | N/A | N/A | 0 | AC Voltage Scale Factor
7 | 7 | 1 | R | FXconfig_Time_SF | int16 | N/A | N/A | -1 | Time Scale Factor
8 | 8 | 1 | R | FXconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Major firmware revision
9 | 9 | 1 | R | FXconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Mid firmware revision
10 | 10 | 1 | R | FXconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | Inverter Minor firmware revision
11 | 11 | 1 | R/W | FXconfig_Absorb_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Absorb Voltage Target
12 | 12 | 1 | R/W | FXconfig_Absorb_Time_Hours | uint16 | Hours | FXconfig_Time_SF | Programmable | Absorb Time Hours
13 | 13 | 1 | R/W | FXconfig_Float_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Float Voltage Target
14 | 14 | 1 | R/W | FXconfig_Float_Time_Hours | uint16 | Hours | FXconfig_Time_SF | Programmable | Float Time Hours
15 | 15 | 1 | R/W | FXconfig_ReFloat_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | ReFloat Voltage Target
16 | 16 | 1 | R/W | FXconfig_EQ_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | EQ Voltage Target
17 | 17 | 1 | R/W | FXconfig_EQ_Time_Hours | uint16 | Hours | FXconfig_Time_SF | Programmable | EQ Time Hours
18 | 18 | 1 | R/W | FXconfig_Search_Sensitivity | uint16 | N/A | N/A | Programmable | Search sensitivity
19 | 19 | 1 | R/W | FXconfig_Search_Pulse_Length | uint16 | Cycles | N/A | Programmable | Search pulse length
20 | 20 | 1 | R/W | FXconfig_Search_Pulse_Spacing | uint16 | Cycles | N/A | Programmable | Search pulse spacing
21 | 21 | 1 | R/W | FXconfig_AC_Input_Type | uint16 | Enumerated | N/A | Programmable | 0=Grid, 1=Gen, 2=Grid Zero
22 | 22 | 1 | R/W | Fxconfig_Input_Support | uint16 | Enumerated | N/A | Programmable | 1=Yes, 0=No (only valid if AC Input Type is Gen)
23 | 23 | 1 | R/W | FXconfig_Grid_AC_Input_Current_Limit | uint16 | Amps | FXconfig_AC_Current_SF | Programmable | Grid AC input current limit
24 | 24 | 1 | R/W | FXconfig_Gen_AC_Input_Current_Limit | uint16 | Amps | FXconfig_AC_Current_SF | Programmable | Gen AC input current limit
25 | 25 | 1 | R/W | FXconfig_Charger_AC_Input_Current_Limit | uint16 | Amps | FXconfig_AC_Current_SF | Programmable | Charger AC input current limit
26 | 26 | 1 | R/W | FXconfig_Charger_Operating_Mode | uint16 | Enumerated | N/A | Programmable | 0=Charger Off, 1=Charger Auto, 2=Charger On
27 | 27 | 1 | R/W | FXconfig_Grid_Lower_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage lower limit
28 | 28 | 1 | R/W | FXconfig_Grid_Upper_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Grid Input AC voltage upper limit
29 | 29 | 1 | R/W | FXconfig_Grid_Transfer_Delay | uint16 | Minutes | N/A | Programmable | Grid Input AC connect delay
30 | 30 | 1 | R/W | FXconfig_Gen_Lower_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage lower limit
31 | 31 | 1 | R/W | FXconfig_Gen_Upper_Input_Voltage_Limit | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | Gen Input AC voltage upper limit
32 | 32 | 1 | R/W | FXconfig_Gen_Transfer_Delay | uint16 | Cycles | N/A | Programmable | Gen Input AC transfer delay
33 | 33 | 1 | R/W | FXconfig_Gen_Connect_Delay | uint16 | Minutes | FXconfig_Time_SF | Programmable | Gen Input AC connect delay
34 | 34 | 1 | R/W | FXconfig_AC_Output_Voltage | uint16 | Volts AC | FXconfig_AC_Voltage_SF | Programmable | AC output Voltage
35 | 35 | 1 | R/W | FXconfig_Low_Battery_Cut_Out_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Battery cut-out voltage
36 | 36 | 1 | R/W | FXconfig_Low_Battery_Cut_In_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Battery cut-in voltage
37 | 37 | 1 | R/W | FXconfig_AUX_Mode | uint16 | Enumerated | N/A | Programmable | 0=Remote, 1=Load Shed, 2=Gen Alert, 3=Fault, 4=Vent Fan, 5=Cool Fan, 6=Divert DC, 7=Divert AC, 8=AC Drop
38 | 38 | 1 | R/W | FXconfig_AUX_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = On; 2 = Auto
39 | 39 | 1 | R/W | FXconfig_AUX_Load_Shed_Enable_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Load Shed enable voltage
40 | 40 | 1 | R/W | FXconfig_AUX_Gen_Alert_On_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Gen Alert On voltage
41 | 41 | 1 | R/W | FXconfig_AUX_Gen_Alert_On_Delay | uint16 | Minutes | N/A | Programmable | Gen Alert On delay minutes
42 | 42 | 1 | R/W | FXconfig_AUX_Gen_Alert_Off_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Gen Alert Off voltage
43 | 43 | 1 | R/W | FXconfig_AUX_Gen_Alert_Off_Delay | uint16 | Minutes | N/A | Programmable | Gen Alert Off delay minutes
44 | 44 | 1 | R/W | FXconfig_AUX_Vent_Fan_Enable_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Vent Fan enable voltage
45 | 45 | 1 | R/W | FXconfig_AUX_Vent_Fan_Off_Period | uint16 | Minutes | N/A | Programmable | Van Fan Off delay minutes
46 | 46 | 1 | R/W | FXconfig_AUX_Divert_Enable_Voltage | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | DC Divert enable voltage
47 | 47 | 1 | R/W | FXconfig_AUX_Divert_Off_Delay | uint16 | Minutes | N/A | Programmable | Divert Off delay minutes
48 | 48 | 1 | R | FXconfig_Stacking_Mode | uint16 | Enumerated | N/A | Read Only | 0=1-2phase Master, 1=Classic Slave, 2=OB Slave L1, 3=OB Slave L2, 4=3phase Master, 5=3phase Slave,10=Master, 11=Classic Slave, 12=OB Slave L1, 13=OB Slave L2, 14=3phase OB Slave A, 15=3phase OB Slave B, 16=3phase OB Slave C, 17=3phase Classic B, 18=3phase Classic C, 19=Independent
49 | 49 | 1 | R/W | FXconfig_Master_Power_Save_Level | uint16 | N/A | N/A | Programmable | Master inverter power save level
50 | 50 | 1 | R/W | FXconfig_Slave_Power_Save_Level | uint16 | N/A | N/A | Programmable | Slave inverter power save level
51 | 51 | 1 | R/W | FXconfig_Sell_Volts | uint16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Sell Voltage Target
52 | 52 | 1 | R/W | FXconfig_Grid_Tie_Window | uint16 | Enumerated | N/A | Programmable | 0=IEEE, 1=User
53 | 53 | 1 | R/W | FXconfig_Grid_Tie_Enable | uint16 | Enumerated | N/A | Programmable | 1=Yes, 0=No
54 | 54 | 1 | R/W | FXconfig_AC_Input_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | AC input voltage calibration factor
55 | 55 | 1 | R/W | FXconfig_AC_Output_Voltage_Calibrate_Factor | int16 | Volts AC | N/A | Programmable | AC output voltage calibration factor
56 | 56 | 1 | R/W | FXconfig_Battery_Voltage_Calibrate_Factor | int16 | DC Volts | FXconfig_DC_Voltage_SF | Programmable | Battery voltage calibration factor
57 | 65 | 9 | R | FXconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
66 | 74 | 9 | R | FXconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
Table 9 FLEXnet-DC Configuration Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | FNconfig_DID | uint16 | N/A | N/A | 64119 | Vendor Extension for OutBack FLEXnet-DC Battery Monitor Configuration Block
2 | 2 | 1 | R | FNconfig_Length | uint16 | Registers | N/A | 52 | Length of block in 16-bit registers
3 | 3 | 1 | R | FNconfig_Port_Number | uint16 | N/A | N/A | 1-10 | Port number on OutBack network
4 | 4 | 1 | R | FNconfig_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | FNconfig_DC_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
6 | 6 | 1 | R | FNconfig_kWh_SF | int16 | N/A | N/A | -2 | Kilo Watt Hours Scale Factor
7 | 7 | 1 | R | FNconfig_Major_Firmware_Number | uint16 | N/A | N/A | Read Only | FLEXnet-DC Major firmware revision
8 | 8 | 1 | R | FNconfig_Mid_Firmware_Number | uint16 | N/A | N/A | Read Only | FLEXnet-DC Mid firmware revision
9 | 9 | 1 | R | FNconfig_Minor_Firmware_Number | uint16 | N/A | N/A | Read Only | FLEXnet-DC Minor firmware revision
10 | 10 | 1 | R/W | FNconfig_Battery_Capacity | uint16 | AH | N/A | Programmable | Battery AH capacity
11 | 11 | 1 | R/W | FNconfig_Charged_Volts | uint16 | DC Volts | FNconfig_DC_Voltage_SF | Programmable | Battery Charged Voltage
12 | 12 | 1 | R/W | FNconfig_Charged_Time | uint16 | Minutes | N/A | Programmable | Battery Charged Time Minutes
13 | 13 | 1 | R/W | FNconfig_Battery_Charged_Amps | uint16 | Amps | FNconfig_DC_Current_SF | Programmable | Battery Charged Return Amps
14 | 14 | 1 | R/W | FNconfig_Charge_Factor | uint16 | Percent | N/A | Programmable | Battery Charge Factor
15 | 15 | 1 | R/W | FNconfig_Shunt_A_Enabled | uint16 | Enumerated | N/A | Programmable | 0=Enabled, 1=Disabled
16 | 16 | 1 | R/W | FNconfig_Shunt_B_Enabled | uint16 | Enumerated | N/A | Programmable | 0=Enabled, 1=Disabled
17 | 17 | 1 | R/W | FNconfig_Shunt_C_Enabled | uint16 | Enumerated | N/A | Programmable | 0=Enabled, 1=Disabled
18 | 18 | 1 | R/W | FNconfig_Relay_Control | uint16 | Enumerated | N/A | Programmable | 0 = Off; 1 = Auto; 2 = On
19 | 19 | 1 | R/W | FNconfig_Relay_Invert_Logic | uint16 | Enumerated | N/A | Programmable | 0=Invert Logic,1=Normal
20 | 20 | 1 | R/W | FNconfig_Relay_High_Voltage | uint16 | DC Volts | FNconfig_DC_Voltage_SF | Programmable | Relay high voltage enable
21 | 21 | 1 | R/W | FNconfig_Relay_Low_Voltage | uint16 | DC Volts | FNconfig_DC_Voltage_SF | Programmable | Relay low voltage enable
22 | 22 | 1 | R/W | FNconfig_Relay_SOC_High | uint16 | Percent | N/A | Programmable | Relay high SOC enable
23 | 23 | 1 | R/W | FNconfig_Relay_SOC_Low | uint16 | Percent | N/A | Programmable | Relay low SOC enable
24 | 24 | 1 | R/W | FNconfig_Relay_High_Enable_Delay | uint16 | Minutes | N/A | Programmable | Relay High Enable Delay
25 | 25 | 1 | R/W | FNconfig_Relay_Low_Enable_Delay | uint16 | Minutes | N/A | Programmable | Relay Low Enable Delay
26 | 26 | 1 | R/W | FNconfig_Set_Data_Log_Day_Offset | uint16 | Days | N/A | Programmable | Day offset 0-400, 0 =Today, 1 = -1 day …
27 | 27 | 1 | R | FNconfig_Get_Current_Data_Log_Day_Offset | uint16 | Days | N/A | Read Only | Current Data Log Day Offset
28 | 28 | 1 | R | FNconfig_Datalog_Minimum_SOC | uint16 | Percent | N/A | Read Only | Datalog minimum SOC
29 | 29 | 1 | R | FNconfig_Datalog_Input_AH | uint16 | AH | N/A | Read Only | Datalog input AH
30 | 30 | 1 | R | FNconfig_Datalog_Input_kWh | uint16 | kWh | FNconfig_kWh_SF | Read Only | Datalog input kWh
31 | 31 | 1 | R | FNconfig_Datalog_Output_AH | uint16 | AH | N/A | Read Only | Datalog output AH
32 | 32 | 1 | R | FNconfig_Datalog_Output_kWh | uint16 | kWh | FNconfig_kWh_SF | Read Only | Datalog output kWh
33 | 33 | 1 | R | FNconfig_Datalog_NET_AH | uint16 | AH | N/A | Read Only | Datalog NET AH
34 | 34 | 1 | R | FNconfig_Datalog_NET_kWh | uint16 | kWh | FNconfig_kWh_SF | Read Only | Datalog NET kWh
35 | 35 | 1 | R | FNconfig_Clear_Data_Log_Read | uint16 | N/A | N/A | Read Only | Read value needed to clear data log
35 | 35 | 1 | W | FNconfig_Clear_Data_Log_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear data log
36 | 36 | 1 | W | FNconfig_Clear_Data_Log_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to clear data log
37 | 45 | 9 | R | FNconfig_Serial_Number | string (18) | N/A | N/A | Read Only | Device serial number
46 | 54 | 9 | R | FNconfig_Model_Number | string (18) | N/A | N/A | Read Only | Device model
Table 10 FLEXnet-DC Real Time Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | FN_DID | uint16 | N/A | N/A | 64118 | Vendor Extension for OutBack FLEXnet DC Battery Monitor Status Block
2 | 2 | 1 | R | FN_Length | uint16 | Registers | N/A | 76 | Length of block in 16-bit registers
3 | 3 | 1 | R | FN_Port_Number | uint16 | N/A | N/A | 1-10 | Port number on Outback network
4 | 4 | 1 | R | FN_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
5 | 5 | 1 | R | FN_DC_Current_SF | int16 | N/A | N/A | -1 | DC Current Scale Factor
6 | 6 | 1 | R | FN_Time_SF | int16 | N/A | N/A | -1 | Time Scale Factor
7 | 7 | 1 | R | FN_kWh_SF | int16 | N/A | N/A | -2 | Kilo Watt Hours Scale Factor
8 | 8 | 1 | R | FN_kW_SF | int16 | N/A | N/A | -2 | Kilo Watt Scale Factor
9 | 9 | 1 | R | FN_Shunt_A_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt A current
10 | 10 | 1 | R | FN_Shunt_B_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt B current
11 | 11 | 1 | R | FN_Shunt_C_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt C current
12 | 12 | 1 | R | FN_Battery_Voltage | uint16 | Volts | FN_DC_Voltage_SF | Read Only | Battery Voltage
13 | 13 | 1 | R | FN_Battery_Current | int16 | Amps | FN_DC_Current_SF | Read Only | Battery Current
14 | 14 | 1 | R | FN_Battery_Temperature | int16 | Degrees C | N/A | Read Only | Battery Temperature C
15 | 15 | 1 | R | FN_Status_Flags | uint16 | Bitfield | N/A | Read Only | See FN Status Table
16 | 16 | 1 | R | FN_Shunt_A_Accumulated_AH | int16 | AH | N/A | Read Only | Shunt A Accumulated_AH
17 | 17 | 1 | R | FN_Shunt_A_Accumulated_kWh | int16 | kWh | FN_kWh_SF | Read Only | Shunt A Accumulated_kWh
18 | 18 | 1 | R | FN_Shunt_B_Accumulated_AH | int16 | AH | N/A | Read Only | Shunt B Accumulated_AH
19 | 19 | 1 | R | FN_Shunt_B_Accumulated_kWh | int16 | kWh | FN_kWh_SF | Read Only | Shunt B Accumulated_kWh
20 | 20 | 1 | R | FN_Shunt_C_Accumulated_AH | int16 | AH | N/A | Read Only | Shunt C Accumulated_AH
21 | 21 | 1 | R | FN_Shunt_C_Accumulated_kWh | int16 | kWh | FN_kWh_SF | Read Only | Shunt C Accumulated_kWh
22 | 22 | 1 | R | FN_Input_Current | uint16 | Amps | FN_DC_Current_SF | Read Only | Total_input_current
23 | 23 | 1 | R | FN_Output_Current | uint16 | Amps | FN_DC_Current_SF | Read Only | Total_output_current
24 | 24 | 1 | R | FN_Input_kW | uint16 | kW | FN_kW_SF | Read Only | Total_input_kWatts
25 | 25 | 1 | R | FN_Output_kW | uint16 | kW | FN_kW_SF | Read Only | Total_output_kWatts
26 | 26 | 1 | R | FN_Net_kW | int16 | kW | FN_kW_SF | Read Only | Total_net_kWatts
27 | 27 | 1 | R | FN_Days_Since_Charge_Parameters_Met | uint16 | Days | FN_Time_SF | Read Only | Days Since Charge Parameters Met
28 | 28 | 1 | R | FN_State_Of_Charge | uint16 | Percent | N/A | Read Only | Current Battery State of Charge
29 | 29 | 1 | R | FN_Todays_Minimum_SOC | uint16 | Percent | N/A | Read Only | Todays minimum SOC
30 | 30 | 1 | R | FN_Todays_Maximum_SOC | uint16 | Percent | N/A | Read Only | Todays maximum SOC
31 | 31 | 1 | R | FN_Todays_NET_Input_AH | uint16 | AH | N/A | Read Only | Todays NET input AH
32 | 32 | 1 | R | FN_Todays_NET_Input_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Todays NET input kWh
33 | 33 | 1 | R | FN_Todays_NET_Output_AH | uint16 | AH | N/A | Read Only | Todays NET output AH
34 | 34 | 1 | R | FN_Todays_NET_Output_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Todays NET output kWh
35 | 35 | 1 | R | FN_Todays_NET_Battery_AH | int16 | AH | N/A | Read Only | Todays NET battery AH
36 | 36 | 1 | R | FN_Todays_NET_Battery_kWh | int16 | kWh | FN_kWh_SF | Read Only | Todays NET battery kWh
37 | 37 | 1 | R | FN_Charge_Factor_Corrected_NET_Battery_AH | int16 | AH | N/A | Read Only | Charge factor corrected NET battery AH
38 | 38 | 1 | R | FN_Charge_Factor_Corrected_NET_Battery_kWh | int16 | kWh | FN_kWh_SF | Read Only | Charge factor corrected NET battery kWh
39 | 39 | 1 | R | FN_Todays_Minimum_Battery_Voltage | uint16 | Volts | FN_DC_Voltage_SF | Programmable | Todays minimum battery voltage
40 | 41 | 2 | R | FN_Todays_Minimum_Battery_Time | uint32 | Seconds | N/A | Read Only | Todays minimum battery voltage time UTC
42 | 42 | 1 | R | FN_Todays_Maximum_Battery_Voltage | uint16 | Volts | FN_DC_Voltage_SF | Programmable | Todays maximum battery voltage
43 | 44 | 2 | R | FN_Todays_Maximum_Battery_Time | uint32 | Seconds | N/A | Read Only | Todays maximum battery voltage time UTC
45 | 45 | 1 | R | FN_Cycle_Charge_Factor | uint16 | Percent | N/A | Read Only | Cycle Charge Factor
46 | 46 | 1 | R | FN_Cycle_kWh_Charge_Efficiency | uint16 | Percent | N/A | Read Only | Cycle kWh Charge Efficiency
47 | 47 | 1 | R | FN_Total_Days_At_100_Percent | uint16 | Days | FN_Time_SF | Programmable | Total days at 100% charged
48 | 48 | 1 | R | FN_Lifetime_kAH_Removed | uint16 | AH | N/A | Programmable | Lifetime kAH removed from battery
49 | 49 | 1 | R | FN_Shunt_A_Historical_Returned_To_Battery_AH | uint16 | AH | N/A | Read Only | Shunt A historical returned to battery AH
50 | 50 | 1 | R | FN_Shunt_A_Historical_Returned_To_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt A historical returned to battery kWh
51 | 51 | 1 | R | FN_Shunt_A_Historical_Removed_From_Battery_AH | uint16 | AH | N/A | Read Only | Shunt A historical removed from battery AH
52 | 52 | 1 | R | FN_Shunt_A_Historical_Removed_From_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt A historical removed from battery kWh
53 | 53 | 1 | R | FN_Shunt_A_Maximum_Charge_Rate | uint16 | Amps | FN_DC_Current_SF | Read Only | Shunt A historical maximum charge rate Amps
54 | 54 | 1 | R | FN_Shunt_A_Maximum_Charge_Rate_kW | uint16 | kW | FN_kWh_SF | Read Only | Shunt A historical maximum charge rate kW
55 | 55 | 1 | R | FN_Shunt_A_Maximum_Discharge_Rate | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt A historical maximum discharge rate Amps
56 | 56 | 1 | R | FN_Shunt_A_Maximum_Discharge_Rate_kW | int16 | kW | FN_kWh_SF | Read Only | Shunt A historical maximum discharge rate kW
57 | 57 | 1 | R | FN_Shunt_B_Historical_Returned_To_Battery_AH | uint16 | AH | N/A | Read Only | Shunt B historical returned to battery AH
58 | 58 | 1 | R | FN_Shunt_B_Historical_Returned_To_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt B historical returned to battery kWh
59 | 59 | 1 | R | FN_Shunt_B_Historical_Removed_From_Battery_AH | uint16 | AH | N/A | Read Only | Shunt B historical removed from battery AH
60 | 60 | 1 | R | FN_Shunt_B_Historical_Removed_From_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt B historical removed from battery kWh
61 | 61 | 1 | R | FN_Shunt_B_Maximum_Charge_Rate | uint16 | Amps | FN_DC_Current_SF | Read Only | Shunt B historical maximum charge rate Amps
62 | 62 | 1 | R | FN_Shunt_B_Maximum_Charge_Rate_kW | uint16 | kW | FN_kWh_SF | Read Only | Shunt B historical maximum charge rate kW
63 | 63 | 1 | R | FN_Shunt_B_Maximum_Discharge_Rate | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt B historical maximum discharge rate Amps
64 | 64 | 1 | R | FN_Shunt_B_Maximum_Discharge_Rate_kW | int16 | kW | FN_kWh_SF | Read Only | Shunt B historical maximum discharge rate kW
65 | 65 | 1 | R | FN_Shunt_C_Historical_Returned_To_Battery_AH | uint16 | AH | N/A | Read Only | Shunt C historical returned to battery AH
66 | 66 | 1 | R | FN_Shunt_C_Historical_Returned_To_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt C historical returned to battery kWh
67 | 67 | 1 | R | FN_Shunt_C_Historical_Removed_From_Battery_AH | uint16 | AH | N/A | Read Only | Shunt C historical removed from battery AH
68 | 68 | 1 | R | FN_Shunt_C_Historical_Removed_From_Battery_kWh | uint16 | kWh | FN_kWh_SF | Read Only | Shunt C historical removed from battery kWh
69 | 69 | 1 | R | FN_Shunt_C_Maximum_Charge_Rate | uint16 | Amps | FN_DC_Current_SF | Read Only | Shunt C historical maximum charge rate Amps
70 | 70 | 1 | R | FN_Shunt_C_Maximum_Charge_Rate_kW | uint16 | kW | FN_kWh_SF | Read Only | Shunt C historical maximum charge rate kW
71 | 71 | 1 | R | FN_Shunt_C_Maximum_Discharge_Rate | int16 | Amps | FN_DC_Current_SF | Read Only | Shunt C historical maximum discharge rate Amps
72 | 72 | 1 | R | FN_Shunt_C_Maximum_Discharge_Rate_kW | int16 | kW | FN_kWh_SF | Read Only | Shunt C historical maximum discharge rate kW
73 | 73 | 1 | R | FN_Shunt_A_Reset_Maximum_Data | uint16 | N/A | N/A | Read Only | Read value needed to reset shunt A maximum data
74 | 74 | 1 | W | FN_Shunt_A_Reset_Maximum_Data_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to reset shunt A maximum data
75 | 75 | 1 | R | FN_Shunt_B_Reset_Maximum_Data | uint16 | N/A | N/A | Read Only | Read value needed to reset shunt B maximum data
76 | 76 | 1 | W | FN_Shunt_B_Reset_Maximum_Data_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to reset shunt B maximum data
77 | 77 | 1 | R | FN_Shunt_C_Reset_Maximum_Data | uint16 | N/A | N/A | Read Only | Read value needed to reset shunt C maximum data
78 | 78 | 1 | W | FN_Shunt_C_Reset_Maximum_Data_Write_Complement | uint16 | N/A | N/A | Write Only | Write value's complement to reset shunt C maximum data
FN_Status Table
[8 empty] | Contents | Description
[8 empty] | 0x0001 | AUX relay enabled
[8 empty] | 0x0002 | Charge Parameters Met
Table 11 OutBack System Control Block
Start | End | Size | R/W | Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | OB_DID | uint16 | N/A | N/A | 64120 | Vendor Extension for OutBack System Control Block
2 | 2 | 1 | R | OB_Length | uint16 | Registers | N/A | 25 | Length of block in 16-bit registers
3 | 3 | 1 | R | OB_DC_Voltage_SF | int16 | N/A | N/A | -1 | DC Voltage Scale Factor
4 | 4 | 1 | R | OB_AC_Current_SF | int16 | N/A | N/A | -1 | AC Current Scale Factor
5 | 5 | 1 | R | OB_Time_SF | int16 | N/A | N/A | -1 | Charge Time Scale Factor
6 | 6 | 1 | W | OB_Bulk_Charge_Enable_Disable | uint16 | Enumerated | N/A | Programmable | 1=Start Bulk, 2=Stop Bulk, 3=Start EQ Charge, 4= Stop EQ Charge
7 | 7 | 1 | W | OB_Inverter_AC_Drop_Use | uint16 | Enumerated | N/A | Programmable | 1=Use, 2=Drop
8 | 8 | 1 | W | OB_Set_Inverter_Mode | uint16 | Enumerated | N/A | Programmable | 1=Off, 2=Search, 3=On
9 | 9 | 1 | W | OB_Grid_Tie_Mode | uint16 | Enumerated | N/A | Programmable | 1=Enable, 2=Disable
10 | 10 | 1 | W | OB_Set_Inverter_Charger_Mode | uint16 | Enumerated | N/A | Programmable | 1=Off, 2=Auto, 3=On
11 | 11 | 1 | R | OB_Control_Status | uint16 | Bitfield | N/A | N/A | Bit field for status. See OB_Control_Status Table
12 | 12 | 1 | R/W | OB_Set_Sell_Voltage | uint16 | Volts | OB_DC_Voltage_SF | Programmable | Global Sell Voltage
13 | 13 | 1 | R/W | OB_Set_Radian_Inverter_Sell_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Radian Inverter Sell Current Limit
14 | 14 | 1 | R/W | OB_Set_Absorb_Voltage | uint16 | Volts | OB_DC_Voltage_SF | Programmable | Global Absorb Voltage
15 | 15 | 1 | R/W | OB_Set_Absorb_Time | uint16 | Hours | OB_Time_SF | Programmable | Time in tenths of hour
16 | 16 | 1 | R/W | OB_Set_Float_Voltage | uint16 | Volts | OB_DC_Voltage_SF | Programmable | Global Float Voltage
17 | 17 | 1 | R/W | OB_Set_Float_Time | uint16 | Hours | OB_Time_SF | Programmable | Time in tenths of hour
18 | 18 | 1 | R/W | OB_Set_Inverter_Charger_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Inverter Charger Current Limit
19 | 19 | 1 | R/W | OB_Set_Inverter_AC1_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Inverter AC1 input Current Limit
20 | 20 | 1 | R/W | OB_Set_Inverter_AC2_Current_Limit | uint16 | Amps | OB_AC_Current_SF | Programmable | Inverter AC2 input Current Limit
21 | 21 | 1 | R/W | OB_Set_AGS_OP_Mode | uint16 | Enumerated | N/A | Programmable | AGS Operating Mode: 0=Off, 1=On, 2=Auto
22 | 22 | 1 | R | OB_AGS_Operational_State | uint16 | Enumerated | N/A | N/A | GEN_STOP=0, GEN_STARTING=1, GEN_RUNNING=2, GEN_WARMUP=3, GEN_COOLDOWN=4, GEN_AWAITING_AC=5
23 | 23 | 1 | R | OB_AGS_Operational_State_Timer | uint16 | Seconds | N/A | Measured | Number of seconds that OB_AGS_Operational_State has been in current state. If Operational State is 0 then timer=0
24 | 25 | 2 | R | OB_Gen_Last_Run_Start_Time_GMT | uint32 | Seconds | N/A | Measured | Generator last start time in GMT seconds
26 | 27 | 2 | R | OB_Gen_Last_Start_Run_Duration | uint32 | Seconds | N/A | Measured | Last Generator Start Run Duration Seconds
OB_Control_Status Table
[8 empty] | Contents | Description
[8 empty] | Contents | Description
[8 empty] | 0x0001 | Bulk Charging
[8 empty] | 0x0002 | Float Charging
[8 empty] | 0x0004 | Inverter AC Input Use
[8 empty] | 0x0008 | Inverter Off
[8 empty] | 0x0010 | Inverter Search Mode
[8 empty] | 0x0020 | Inverter On
[8 empty] | 0x0040 | Inverter Grid-Tie Enabled
[8 empty] | 0x0080 | Inverter Charger Disabled
[8 empty] | 0x0100 | Inverter Charger Auto Mode
[8 empty] | 0x0200 | Inverter Charger Bulk and Float Mode
[8 empty] | 0x0400 | EQ Charging
Table 12 SunSpec Common Model Block
Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 1 | Uniquely identifies this as a SunSpec Common Model block
2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 65 | Length of block in 16-bit registers
3 | 18 | 16 | R | C_Manufacturer | string (32) | N/A | N/A | Read Only
19 | 34 | 16 | R | C_Model | string (32) | N/A | N/A | Read Only
35 | 42 | 8 | R | C_Options | string (16) | N/A | N/A | Read Only
43 | 50 | 8 | R | C_Version | string (16) | N/A | N/A | Read Only
51 | 66 | 16 | R | C_SerialNumber | string (32) | N/A | N/A | Read Only
67 | 67 | 1 | R/W | C_DeviceAddress | uint16 | N/A | N/A | Write Only
Table 13 SunSpec Inverter - Single Phase
Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 101 | Uniquely identifies this as a SunSpec Single Phase Inverter
2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 50 | Length of model block
3 | 3 | 1 | R | I_AC_Current | uint16 | Amps | I_AC_Current_SF | Measured | AC Total Current value
4 | 4 | 1 | R | I_AC_CurrentA | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-A Current value
5 | 5 | 1 | R | I_AC_CurrentB | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-B Current value
6 | 6 | 1 | R | I_AC_CurrentC | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-C Current value
7 | 7 | 1 | R | I_AC_Current_SF | int16 | SF | N/A |  | AC Current Scale factor
8 | 8 | 1 | R | I_AC_VoltageAB | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-AB value
9 | 9 | 1 | R | I_AC_VoltageBC | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase BC value
10 | 10 | 1 | R | I_AC_VoltageCA | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase CA value
11 | 11 | 1 | R | I_AC_VoltageAN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-A-to-neutral value
12 | 12 | 1 | R | I_AC_VoltageBN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase B-to-neutral value
13 | 13 | 1 | R | I_AC_VoltageCN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase C-to-neutral value
14 | 14 | 1 | R | I_AC_Voltage_SF | int16 | SF | N/A |  | AC Voltage Scale factor
15 | 15 | 1 | R | I_AC_Power | int16 | Watts | I_AC_Power_SF | Measured | AC Power value
16 | 16 | 1 | R | I_AC_Power_SF | int16 | SF | N/A |  | AC Power Scale factor
17 | 17 | 1 | R | I_AC_Frequency | uint16 | Hertz | I_AC_Frequency_SF | Measured | AC Frequency value
18 | 18 | 1 | R | I_AC_Frequency_SF | int16 | SF | N/A |  | Scale factor
19 | 19 | 1 | R | I_AC_VA | int16 | VA | I_AC_VA_SF | Measured | Apparent Power
20 | 20 | 1 | R | I_AC_VA_SF | int16 | SF | N/A |  | Scale factor
21 | 21 | 1 | R | I_AC_VAR | int16 | VAR | I_AC_VAR_SF | Measured | Reactive Power
22 | 22 | 1 | R | I_AC_VAR_SF | int16 | SF | N/A |  | Scale factor
23 | 23 | 1 | R | I_AC_PF | int16 | % | I_AC_PF_SF | Measured | Power Factor
24 | 24 | 1 | R | I_AC_PF_SF | int16 | SF | N/A |  | Scale factor
25 | 26 | 2 | R | I_AC_Energy_WH | uint32 | WattHours | I_AC_Energy_WH_SF | Measured | AC Lifetime Energy production
27 | 27 | 1 | R | I_AC_Energy_WH_SF | uint16 | SF | N/A | Measured | AC Lifetime Energy production scale factor
28 | 28 | 1 | R | I_DC_Current | uint16 | Amps | I_DC_Current_SF | Measured | DC Current value
29 | 29 | 1 | R | I_DC_Current_SF | int16 | SF | N/A |  | Scale factor
30 | 30 | 1 | R | I_DC_Voltage | uint16 | Volts | I_DC_Voltage_SF | Measured | DC Voltage value
31 | 31 | 1 | R | I_DC_Voltage_SF | int16 | SF | N/A |  | Scale factor
32 | 32 | 1 | R | I_DC_Power | int16 | Watts | I_DC_Power_SF | Measured | DC Power value
33 | 33 | 1 | R | I_DC_Power_SF | int16 | SF | N/A |  | Scale factor
34 | 34 | 1 | R | I_Temp_Cab | int16 | Degrees C | I_Temp_SF | Measured | Cabinet Temperature
35 | 35 | 1 | R | I_Temp_Sink | int16 | Degrees C | I_Temp_SF | Measured | Coolant or Heat Sink Temperature
36 | 36 | 1 | R | I_Temp_Trans | int16 | Degrees C | I_Temp_SF | Measured | Transformer Temperature
37 | 37 | 1 | R | I_Temp_Other | int16 | Degrees C | I_Temp_SF | Measured | Other Temperature
38 | 38 | 1 | R | I_Temp_SF | int16 | SF | N/A |  | Scale factor
39 | 39 | 1 | R | I_Status | uint16 | Enumerated | N/A | N/A | Operating State
40 | 40 | 1 | R | I_Status_Vendor | uint16 | Enumerated | N/A | N/A | Vendor Defined Operating State
41 | 42 | 2 | R | I_Event_1 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 0-31)
43 | 44 | 2 | R | I_Event_2 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 32-63) Future Use, set to 0
45 | 46 | 2 | R | I_Event_1_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 0-31)
47 | 48 | 2 | R | I_Event_2_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 32-63) Future Use
49 | 50 | 2 | R | I_Event_3_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 64-95) Future Use
51 | 52 | 2 | R | I_Event_4_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 96-127) Future Use
Table 14 SunSpec Inverter - Split Phase
Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 102 | Uniquely identifies this as a SunSpec Split Phase Inverter
2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 50 | Length of model block
3 | 3 | 1 | R | I_AC_Current | uint16 | Amps | I_AC_Current_SF | Measured | AC Total Current value
4 | 4 | 1 | R | I_AC_CurrentA | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-A Current value
5 | 5 | 1 | R | I_AC_CurrentB | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-B Current value
6 | 6 | 1 | R | I_AC_CurrentC | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-C Current value
7 | 7 | 1 | R | I_AC_Current_SF | int16 | SF | N/A |  | AC Current Scale factor
8 | 8 | 1 | R | I_AC_VoltageAB | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-AB value
9 | 9 | 1 | R | I_AC_VoltageBC | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase BC value
10 | 10 | 1 | R | I_AC_VoltageCA | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase CA value
11 | 11 | 1 | R | I_AC_VoltageAN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-A-to-neutral value
12 | 12 | 1 | R | I_AC_VoltageBN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase B-to-neutral value
13 | 13 | 1 | R | I_AC_VoltageCN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase C-to-neutral value
14 | 14 | 1 | R | I_AC_Voltage_SF | int16 | SF | N/A |  | AC Voltage Scale factor
15 | 15 | 1 | R | I_AC_Power | int16 | Watts | I_AC_Power_SF | Measured | AC Power value
16 | 16 | 1 | R | I_AC_Power_SF | int16 | SF | N/A |  | AC Power Scale factor
17 | 17 | 1 | R | I_AC_Frequency | uint16 | Hertz | I_AC_Frequency_SF | Measured | AC Frequency value
18 | 18 | 1 | R | I_AC_Frequency_SF | int16 | SF | N/A |  | Scale factor
19 | 19 | 1 | R | I_AC_VA | int16 | VA | I_AC_VA_SF | Measured | Apparent Power
20 | 20 | 1 | R | I_AC_VA_SF | int16 | SF | N/A |  | Scale factor
21 | 21 | 1 | R | I_AC_VAR | int16 | VAR | I_AC_VAR_SF | Measured | Reactive Power
22 | 22 | 1 | R | I_AC_VAR_SF | int16 | SF | N/A |  | Scale factor
23 | 23 | 1 | R | I_AC_PF | int16 | % | I_AC_PF_SF | Measured | Power Factor
24 | 24 | 1 | R | I_AC_PF_SF | int16 | SF | N/A |  | Scale factor
25 | 26 | 2 | R | I_AC_Energy_WH | uint32 | WattHours | I_AC_Energy_WH_SF | Measured | AC Lifetime Energy production
27 | 27 | 1 | R | I_AC_Energy_WH_SF | uint16 | SF | N/A | Measured | AC Lifetime Energy production scale factor
28 | 28 | 1 | R | I_DC_Current | uint16 | Amps | I_DC_Current_SF | Measured | DC Current value
29 | 29 | 1 | R | I_DC_Current_SF | int16 | SF | N/A |  | Scale factor
30 | 30 | 1 | R | I_DC_Voltage | uint16 | Volts | I_DC_Voltage_SF | Measured | DC Voltage value
31 | 31 | 1 | R | I_DC_Voltage_SF | int16 | SF | N/A |  | Scale factor
32 | 32 | 1 | R | I_DC_Power | int16 | Watts | I_DC_Power_SF | Measured | DC Power value
33 | 33 | 1 | R | I_DC_Power_SF | int16 | SF | N/A |  | Scale factor
34 | 34 | 1 | R | I_Temp_Cab | int16 | Degrees C | I_Temp_SF | Measured | Cabinet Temperature
35 | 35 | 1 | R | I_Temp_Sink | int16 | Degrees C | I_Temp_SF | Measured | Coolant or Heat Sink Temperature
36 | 36 | 1 | R | I_Temp_Trans | int16 | Degrees C | I_Temp_SF | Measured | Transformer Temperature
37 | 37 | 1 | R | I_Temp_Other | int16 | Degrees C | I_Temp_SF | Measured | Other Temperature
38 | 38 | 1 | R | I_Temp_SF | int16 | SF | N/A |  | Scale factor
39 | 39 | 1 | R | I_Status | uint16 | Enumerated | N/A | N/A | Operating State
40 | 40 | 1 | R | I_Status_Vendor | uint16 | Enumerated | N/A | N/A | Vendor Defined Operating State
41 | 42 | 2 | R | I_Event_1 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 0-31)
43 | 44 | 2 | R | I_Event_2 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 32-63) Future Use, set to 0
45 | 46 | 2 | R | I_Event_1_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 0-31)
47 | 48 | 2 | R | I_Event_2_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 32-63) Future Use
49 | 50 | 2 | R | I_Event_3_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 64-95) Future Use
51 | 52 | 2 | R | I_Event_4_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 96-127) Future Use
Table 15 SunSpec Inverter - Three Phase
Start | End | Size | R/W | Field Name | Type | Units | Scale Factor | Contents | Description
1 | 1 | 1 | R | C_SunSpec_DID | uint16 | N/A | N/A | 103 | Uniquely identifies this as a SunSpec Three Phase Inverter
2 | 2 | 1 | R | C_SunSpec_Length | uint16 | Registers | N/A | 50 | Length of model block
3 | 3 | 1 | R | I_AC_Current | uint16 | Amps | I_AC_Current_SF | Measured | AC Total Current value
4 | 4 | 1 | R | I_AC_CurrentA | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-A Current value
5 | 5 | 1 | R | I_AC_CurrentB | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-B Current value
6 | 6 | 1 | R | I_AC_CurrentC | uint16 | Amps | I_AC_Current_SF | Measured | AC Phase-C Current value
7 | 7 | 1 | R | I_AC_Current_SF | int16 | SF | N/A |  | AC Current Scale factor
8 | 8 | 1 | R | I_AC_VoltageAB | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-AB value
9 | 9 | 1 | R | I_AC_VoltageBC | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase BC value
10 | 10 | 1 | R | I_AC_VoltageCA | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase CA value
11 | 11 | 1 | R | I_AC_VoltageAN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase-A-to-neutral value
12 | 12 | 1 | R | I_AC_VoltageBN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase B-to-neutral value
13 | 13 | 1 | R | I_AC_VoltageCN | uint16 | Volts | I_AC_Voltage_SF | Measured | AC Voltage Phase C-to-neutral value
14 | 14 | 1 | R | I_AC_Voltage_SF | int16 | SF | N/A |  | AC Voltage Scale factor
15 | 15 | 1 | R | I_AC_Power | int16 | Watts | I_AC_Power_SF | Measured | AC Power value
16 | 16 | 1 | R | I_AC_Power_SF | int16 | SF | N/A |  | AC Power Scale factor
17 | 17 | 1 | R | I_AC_Frequency | uint16 | Hertz | I_AC_Frequency_SF | Measured | AC Frequency value
18 | 18 | 1 | R | I_AC_Frequency_SF | int16 | SF | N/A |  | Scale factor
19 | 19 | 1 | R | I_AC_VA | int16 | VA | I_AC_VA_SF | Measured | Apparent Power
20 | 20 | 1 | R | I_AC_VA_SF | int16 | SF | N/A |  | Scale factor
21 | 21 | 1 | R | I_AC_VAR | int16 | VAR | I_AC_VAR_SF | Measured | Reactive Power
22 | 22 | 1 | R | I_AC_VAR_SF | int16 | SF | N/A |  | Scale factor
23 | 23 | 1 | R | I_AC_PF | int16 | % | I_AC_PF_SF | Measured | Power Factor
24 | 24 | 1 | R | I_AC_PF_SF | int16 | SF | N/A |  | Scale factor
25 | 26 | 2 | R | I_AC_Energy_WH | uint32 | WattHours | I_AC_Energy_WH_SF | Measured | AC Lifetime Energy production
27 | 27 | 1 | R | I_AC_Energy_WH_SF | uint16 | SF | N/A | Measured | AC Lifetime Energy production scale factor
28 | 28 | 1 | R | I_DC_Current | uint16 | Amps | I_DC_Current_SF | Measured | DC Current value
29 | 29 | 1 | R | I_DC_Current_SF | int16 | SF | N/A |  | Scale factor
30 | 30 | 1 | R | I_DC_Voltage | uint16 | Volts | I_DC_Voltage_SF | Measured | DC Voltage value
31 | 31 | 1 | R | I_DC_Voltage_SF | int16 | SF | N/A |  | Scale factor
32 | 32 | 1 | R | I_DC_Power | int16 | Watts | I_DC_Power_SF | Measured | DC Power value
33 | 33 | 1 | R | I_DC_Power_SF | int16 | SF | N/A |  | Scale factor
34 | 34 | 1 | R | I_Temp_Cab | int16 | Degrees C | I_Temp_SF | Measured | Cabinet Temperature
35 | 35 | 1 | R | I_Temp_Sink | int16 | Degrees C | I_Temp_SF | Measured | Coolant or Heat Sink Temperature
36 | 36 | 1 | R | I_Temp_Trans | int16 | Degrees C | I_Temp_SF | Measured | Transformer Temperature
37 | 37 | 1 | R | I_Temp_Other | int16 | Degrees C | I_Temp_SF | Measured | Other Temperature
38 | 38 | 1 | R | I_Temp_SF | int16 | SF | N/A |  | Scale factor
39 | 39 | 1 | R | I_Status | uint16 | Enumerated | N/A | N/A | Operating State
40 | 40 | 1 | R | I_Status_Vendor | uint16 | Enumerated | N/A | N/A | Vendor Defined Operating State
41 | 42 | 2 | R | I_Event_1 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 0-31)
43 | 44 | 2 | R | I_Event_2 | uint32 | Bitfield | N/A | N/A | Event Flags (bits 32-63) Future Use, set to 0
45 | 46 | 2 | R | I_Event_1_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 0-31)
47 | 48 | 2 | R | I_Event_2_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 32-63) Future Use
49 | 50 | 2 | R | I_Event_3_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 64-95) Future Use
51 | 52 | 2 | R | I_Event_4_Vendor | uint32 | Bitfield | N/A | N/A | Vendor Defined Event Flags (bits 96-127) Future Use